## README
CSCM Tool - legacy to new status code mapping
DRAFT built from 'Statuscode 4XM Rise0B.xlsx' (Main Controller) and 'HC Status Code Number.xlsx' (Hub Controller). Replace the sheets MC and HC with the correct mapping; keep the sheet names and the column names in row 1.
WHAT THIS FILE IS
The tool reads this workbook (cscm_tool/seed_data/legacy_mapping.xlsx) when .st programs are imported. It holds only what the generated programs do NOT carry: the English description (it becomes the title of the Draft), the type (the status category), the up/down counter, the eight named access levels, the troubleshooting text, and the number plan (legacy number -> new number). Whatever a program carries - trigger snapshot, alarm, available group, delays, repeats, reset and stop programs, the user-group numbers - stays in the program and is never taken from here.
RULES
1. Main Controller: 2XM and 3XM share one legacy numbering, so one legacy number maps to one new number. The legacy number of a Main program is the one in its header comment; the program number is the new number and must agree with this file.
2. Hub Controller: the legacy number is the number of the program file; the new number is in the five-digit Hub range (1xxxx). Moving the Hub codes into the Main range later is a systematic change that is to be done in one step with an approval (docs/21-improvement-ideas.md I-75); it is not part of this file.
3. A new number is only valid after it is approved by the StCd Owner, the Chief Engineer and one Administrator (status APPROVED). A row that is not APPROVED or ISSUED is used with a warning in the preview of the import.
4. A legacy number that is not in this file is never numbered automatically: the program is blocked until the number is allocated and approved and the row is added here. The same holds for a row without a type or without a description.
5. parameter_set_delay / parameter_reset_delay: filled only where the source marks a delay with * (a delay that a controller parameter sets; the value is the parameter's value). The tool uses it when the program names the parameter instead of a time, and the Draft keeps the parameter name in its comment. CONFIRM that * means this.
6. The title of a Draft is the English description of the row; the German name from the program is kept in the comment, and the tool checks the two against the sheet Glossary.
SHEETS
MC - Main Controller rows; HC - Hub Controller rows (same columns; cause and directive are the troubleshooting text of the Draft; planning_* are for the project and are not imported)
HC_groups - the number ranges of the Hub functional groups (from the source), used to check the new numbers
Glossary - German terms of the program names and their English forms, for the translation check (DRAFT, to be extended by the owner)
Approvals - the log of approvals of new numbers (the three approvals)
Lists - the allowed values of status and type
STATUS
PROPOSED = in the plan, not approved yet; FROM_PROGRAM = the pair is carried by a generated program; APPROVED = approved by StCd Owner + Chief Engineer + Administrator; ISSUED = the code exists in the catalogue with this number; REJECTED = not to be used.

## MC
legacy_number | new_number | description | functional_group | logical_node | type | up_down_counter | parameter_set_delay | parameter_reset_delay | development | sales | tcc | service | turbine_operator_package | grid_operator | service_partner | customer | cause | directive | planning_priority | planning_estimation | planning_comment | note | status | source
3000 | 1000 | WCNV Frequency converter not ready | Converter | WCNV | Error | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 2
3005 | 1001 | WCNV Conv. fuse tripped | Converter | WCNV | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 3
3010 | 1002 | WCNV Conv. comm.error | Converter | WCNV | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 4
3011 | 1003 | WCNV Conv. SDO transm.error | Converter | WCNV | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 5
3020 | 1004 | WCNV Chopper util. incr. | Converter | WCNV | Warning | No | *0 ms | *500ms | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 6
3021 | 1005 | WCNV Max. chopper util. | Converter | WCNV | Error | No | *0 ms | *500ms | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 7
3030 | 1006 | WCNV Conv. warning | Converter | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 8
3040 | 1007 | WCNV Conv reset after grid restoration | Converter | WCNV | Info | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | See only | See only | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 9
3050 | 1008 | WCNV Freq. conv. speed window | Converter | WCNV | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 10
3060 | 1009 | WCNV Conv. emerg.off type A | Converter | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 11
3061 | 1010 | WCNV Conv. emerg.off type B | Converter | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 12
3062 | 1011 | WCNV Conv. emerg.off type C | Converter | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 13
3063 | 1012 | WCNV Conv. emerg.off type D | Converter | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 14
3064 | 1013 | WCNV Conv. emerg.off type E | Converter | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 15
3065 | 1014 | WCNV Conv. emerg.off type F | Converter | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 16
3090 | 1015 | WCNV Frequency converter spare protection | Converter | WCNV | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 17
3095 | 1016 | WCNV Error converter disconnection | Converter | WCNV | Error | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 18
3096 | 1017 | WCNV Converter disconnection implausible | Converter | WCNV | Error | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 19
3097 | 1018 | WCNV Max. negative active power | Converter | WCNV | Error | No | *5s |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 20
3110 | 1019 | WCNV Frequency converter error | Converter | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 21
3120 | 1020 | WCNV Frequency converter overspeed | Converter | WCNV | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 22
3121 | 1021 | WCNV Conv. underspeed | Converter | WCNV | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 23
3125 | 1022 | WCNV Timeout ready for connection | Converter | WCNV | Error | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 24
3130 | 1023 | WCNV Timeout grid synchronisation | Converter | WCNV | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 25
3140 | 1024 | WCNV Frequency converter operation range | Converter | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 26
3160 | 1025 | WCNV Cable overload | Converter | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 27
3161 | 1026 | WCNV P reduction power cord overl. | Converter | WCNV | Info | No | *10s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 28
3162 | 1027 | WCNV Cable overload stop | Converter | WCNV | Error | No | *12min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 29
3164 | 1028 | WCNV P reduction stator cable overl. | Converter | WCNV | Info | No | *10s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 30
3200 | 1029 | WCNV Frequency converter temp. low | Converter | WCNV | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 31
3201 | 1030 | WCNV Bypass conv. heating mode | Converter | WCNV | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 32
3202 | 1031 | WCNV Timeout converter temp. low | Converter | WCNV | Error | No | *8h |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 33
3210 | 1032 | WCNV Frequency converter load rejection | Converter | WCNV | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 34
3211 | 1033 | WCNV Conv. load shedding (CAN) | Converter | WCNV | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 35
3220 | 1034 | WCNV Reduced power converter | Converter | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 36
3222 | 1035 | WCNV Timeout reduced power conv. | Converter | WCNV | Error | No |  | *10min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 37
3225 | 1036 | WCNV Limit reactive power converter | Converter | WCNV | Warning | No |  | *2min | Department | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 38
3227 | 1037 | WCNV Timeout Q limit converter | Converter | WCNV | Warning | No | *2h |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 39
3250 | 1038 | WCNV No power | Converter | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 40
3255 | 1039 | WCNV Converter power too high | Converter | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 41
3260 | 1040 | WCNV Converter power too low | Converter | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 42
3265 | 1041 | WCNV Converter torque <> setpoint | Converter | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 43
3267 | 1042 | WCNV Calculated torque implausible | Converter | WCNV | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | set delay in the source: '*o ms' (not a time; left empty) | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 44
3270 | 1043 | WCNV Converter torque monitor level 0 | Converter | WCNV | Info | Yes | *2s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 45
3271 | 1044 | WCNV Converter torque monitor level 1 | Converter | WCNV | Error | Yes | *5s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 46
3280 | 1045 | WCNV Conv. COM mode active | Converter | WCNV | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | See only | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 47
3281 | 1046 | WCNV Conv. COM mode stop | Converter | WCNV | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | See only | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 48
3350 | 1047 | WCNV No pressure increase following pump start-up | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 49
3351 | 1048 | WCNV Timeout no pressure increase following pump start-up | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 50
3355 | 1049 | WCNV No temp. rise after heat.coolant on | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 51
3356 | 1050 | WCNV Pump cooling sys. (tower base) diff.press. low | Converter | WCNV | Warning | No | *0 ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 52
3357 | 1051 | WCNV Pump cooling sys. (tower base) diff.press. too low | Converter | WCNV | Error | No | *0 ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 53
3358 | 1052 | WCNV Pump cooling sys. (tower base) diff.press. high | Converter | WCNV | Warning | No | *0 ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 54
3359 | 1053 | WCNV Pump cooling sys. (tower base) diff.press. too high | Converter | WCNV | Error | No | *0 ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 55
3360 | 1054 | WCNV Implaus. act. in conv.cooling system | Converter | WCNV | Warning | No | *0 ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 56
3365 | 1055 | WCNV Fan 1 cool.sys. error | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 57
3366 | 1056 | WCNV Fan 2 cool.sys. error | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 58
3367 | 1057 | WCNV Fan 3 cool.sys. error | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 59
3368 | 1058 | WCNV Fan 4 cool.sys. error | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 60
3370 | 1059 | WCNV Coolant press. low | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 61
3371 | 1060 | WCNV Coolant press. too low | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 62
3372 | 1061 | WCNV Cool sys. press. switch tripped | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 63
3373 | 1062 | WCNV Coolant press. high (with pump on) | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 64
3374 | 1063 | WCNV Coolant press. too high (with pump on) | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 65
3375 | 1064 | WCNV Coolant press. high (with pump off) | Converter | WCNV | Warning | No | *0 ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 66
3376 | 1065 | WCNV Coolant press. too high (with pump on) | Converter | WCNV | Warning | No | *0 ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 67
3377 | 1066 | WCNV 4-20mA coolant press. | Converter | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 68
3378 | 1067 | WCNV Pump coolant inlet press. 4-20mA | Converter | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 69
3380 | 1068 | WCNV Coolant temp. high | Converter | WCNV | Warning | No | *0 ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 70
3381 | 1069 | WCNV P red. incr. conv. coolant temp. | Converter | WCNV | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 71
3385 | 1070 | WCNV Coolant temp. too high | Converter | WCNV | Warning | No | *0 ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 72
3386 | 1071 | WCNV Conv. max. coolant temp. | Converter | WCNV | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 73
3387 | 1072 | WCNV 4-20mA coolant temp. | Converter | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 74
3395 | 1073 | WCNV Pump cooling sys. overload | Converter | WCNV | Error | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 75
3396 | 1074 | WCNV Coolant heating 1&2 overload | Converter | WCNV | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 76
3397 | 1075 | WCNV Heating overload fans 1- 4 cooling sys. | Converter | WCNV | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 77
3455 | 1200 | WCNV Grid loss auxiliary power | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 78
3460 | 1201 | WCNV Grid loss auxiliary power without grid loss net | Grid | WCNV | Error | No | *3s | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 79
3461 | 1202 | WCNV Grid loss without grid loss auxiliary power | Grid | WCNV | Warning | No | *3s | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 80
3500 | 1203 | WCNV Grid loss | Grid | WCNV | Info | No | *0 ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 81
3501 | 1204 | WCNV Grid disconnection for self-protection | Grid | WCNV | Info | No | *0 ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 82
3502 | 1205 | WCNV Timeout grid error | Grid | WCNV | Error | No | *1h |  | SCADA User | See only | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 83
3503 | 1206 | WCNV Zero-seq. syst. volt. high | Grid | WCNV | Info | No | *1s | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 84
3530 | 1207 | WCNV High voltage - level 1 | Grid | WCNV | Info | No | *1s | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 85
3531 | 1208 | WCNV High voltage - level 2 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 86
3532 | 1209 | WCNV Min. voltage cut in | Grid | WCNV | Info | No | *100ms | *1min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 87
3533 | 1210 | WCNV Max. voltage cut in | Grid | WCNV | Info | No | *100ms | *1min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 88
3534 | 1211 | WCNV Repeat voltage dip | Grid | WCNV | Info | No | *0 ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 89
3535 | 1212 | WCNV Low voltage - level 1 | Grid | WCNV | Info | No | *1s | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 90
3536 | 1213 | WCNV Low voltage - level 2 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 91
3537 | 1214 | WCNV Transient fault | Grid | WCNV | Info | No |  | *0 ms | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 92
3540 | 1215 | WCNV High frequency - level 1 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 93
3541 | 1216 | WCNV High frequency - level 2 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 94
3542 | 1217 | WCNV Max. frequency cut in | Grid | WCNV | Info | No | *100ms | *1min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 95
3543 | 1218 | WCNV High frequency - P reduction | Grid | WCNV | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 96
3544 | 1219 | WCNV Time limit high freq. - P red. | Grid | WCNV | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 97
3545 | 1220 | WCNV Low frequency - Level 1 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 98
3546 | 1221 | WCNV Low frequency - level 2 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 99
3547 | 1222 | WCNV Overfrequency | Grid | WCNV | Info | No |  | *10min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 100
3550 | 1223 | WCNV Phase angle | Grid | WCNV | Info | No | *10s |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 101
3551 | 1224 | WCNV Phase angle | Grid | WCNV | Info | No | *10s |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 102
3555 | 1225 | WCNV Current asymmetry | Grid | WCNV | Error | No | *5s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 103
3560 | 1226 | WCNV Voltage asymmetry | Grid | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 104
3562 | 1227 | WCNV Timeout max. freq. cut in | Grid | WCNV | Info | No | *3min | *10min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 105
3570 | 1228 | WCNV Grid error | Grid | WCNV | Info | No |  | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 106
3571 | 1229 | WCNV Low frequency - level 3 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 107
3572 | 1230 | WCNV Low frequency - level 4 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 108
3573 | 1231 | WCNV Low frequency - level 5 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 109
3574 | 1232 | WCNV Low frequency - level 6 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 110
3575 | 1233 | WCNV Minimum grid frequency | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 111
3576 | 1234 | WCNV Min. frequency cut in | Grid | WCNV | Info | No | *1s | *1min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 112
3577 | 1235 | WCNV Underfrequency | Grid | WCNV | Info | No |  | *10min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 113
3581 | 1236 | WCNV High frequency - level 3 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 114
3582 | 1237 | WCNV High frequency - level 4 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 115
3583 | 1238 | WCNV High frequency - level 5 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 116
3584 | 1239 | WCNV High frequency - level 6 | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 117
3585 | 1240 | WCNV Maximum grid frequency | Grid | WCNV | Info | No | *100ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 118
3586 | 1241 | WCNV P reduction frequency prot. | Grid | WCNV | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 119
3590 | 1242 | WCNV Overvoltage | Grid | WCNV | Info | No | *0ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 120
3591 | 1243 | WCNV Transient voltage peak | Grid | WCNV | Info | No |  | *0ms | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 121
3592 | 1244 | WCNV Repeat transient voltage peak | Grid | WCNV | Info | No | *0ms | *3min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 122
3593 | 1245 | WCNV Grid recovery | Grid | WCNV | Info | No |  | *1min | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 123
3594 | 1246 | WCNV No Connection permission | Grid | WCNV | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 124
3595 | 1247 | WCNV Grid parameters implausible | Grid | WCNV | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 125
3630 | 1248 | WCNV VQ protection | Grid | WCNV | Warning | No | *200ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 126
3632 | 1249 | WCNV VQ protection stop | Grid | WCNV | Error | No | *15min | *15min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 127
3640 | 1250 | WCNV Dynamic frequency control | Grid | WCNV | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 128
3642 | 1251 | WCNV End additional power | Grid | WCNV | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 129
3750 | 1252 | WCNV Grid measurement error | Grid | WCNV | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 130
3751 | 1253 | WCNV Initialization grid meas. | Grid | WCNV | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 131
3866 | 1254 | WCNV LV HRC fuses triggered | Grid | WCNV | Error | No |  |  | Department | See only | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 132
3869 | 1255 | WCNV Lightning protect. transf. Defect | Grid | WCNV | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 133
3898 | 1256 | WCNV Max. transformer temp. PT100 | Grid | WCNV | Error | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 134
3901 | 1257 | WCNV Timeout max. transf. temp. | Grid | WCNV | Error | No | *30min |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WCNV, row 135
2515 | 2000 | WGEN Implausible gen. speed leap | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 2
2520 | 2001 | WGEN Gen.speed analog<>gear.speed | Generator | WGEN | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 3
2521 | 2002 | WGEN Gen.sp.analog <<>> gearb.sp. | Generator | WGEN | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 4
2540 | 2003 | WGEN Gen.speed pulse error | Generator | WGEN | Error | Yes |  | *5s | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 5
2541 | 2004 | WGEN Gen.speed voltage error | Generator | WGEN | Error | No |  | *5s | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 6
2550 | 2005 | WGEN Overload generator fan 1 | Generator | WGEN | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 7
2600 | 2006 | WGEN High temp. gen. bearing 1 | Generator | WGEN | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 8
2605 | 2007 | WGEN Max. temp. gen. bearing 1 | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 9
2607 | 2008 | WGEN PT100 gen. bearing 1 defect | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 10
2608 | 2009 | WGEN Error measuring temp. gen. bearing 1 | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 11
2610 | 2010 | WGEN High temp. gen. bearing 2 | Generator | WGEN | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 12
2615 | 2011 | WGEN Max. temp. gen. bearing 2 | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 13
2617 | 2012 | WGEN PT100 gen. bearing 2 defect | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 14
2618 | 2013 | WGEN Error measuring temp. gen. bearing 2 | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 15
2650 | 2014 | WGEN Overload generator fan 2 | Generator | WGEN | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 16
2655 | 2015 | WGEN Overload generator fan 3 | Generator | WGEN | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 17
2660 | 2016 | WGEN Thermistor generator | Generator | WGEN | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 18
2662 | 2017 | WGEN PT100 stator temp. 2 defect | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 19
2663 | 2018 | WGEN Error measuring temp. 2 stator | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 20
2665 | 2019 | WGEN High stator temperature | Generator | WGEN | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 21
2666 | 2020 | WGEN High stator temperature 2 | Generator | WGEN | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 22
2670 | 2021 | WGEN Max. temp. stator | Generator | WGEN | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 23
2671 | 2022 | WGEN Max. temp. stator 2 | Generator | WGEN | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 24
2672 | 2023 | WGEN PT100 stator temp. defect | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 25
2673 | 2024 | WGEN Error measuring temp. stator | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 26
2674 | 2025 | WGEN Overload generator heating | Generator | WGEN | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 27
2675 | 2026 | WGEN Overload gen. heating: stop | Generator | WGEN | Error | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 28
2685 | 2027 | WGEN Slipring cell temp. high | Generator | WGEN | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 29
2687 | 2028 | WGEN Max. slip ring cell temp. | Generator | WGEN | Error | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 30
2689 | 2029 | WGEN PT100 slipring temp. defect | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 31
2691 | 2030 | WGEN Error measuring temp. stato+ | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 32
2695 | 2031 | WGEN P red. incr. gen. coolant temp. | Generator | WGEN | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 33
2696 | 2032 | WGEN Gen. max. coolant temp. | Generator | WGEN | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 34
2710 | 2033 | WGEN Generator power too high | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 35
2800 | 2034 | WGEN Max. power peak | Generator | WGEN | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 36
2810 | 2035 | WGEN Service generator brushes | Generator | WGEN | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 37
2811 | 2036 | WGEN Fault generator brushes | Generator | WGEN | Error | No |  |  | SCADA User | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 38
2822 | 2037 | WGEN Overload lubrication generator | Generator | WGEN | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 39
2823 | 2038 | WGEN Fault gen. bearing lubrication | Generator | WGEN | Warning | No |  |  | SCADA User | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 40
2826 | 2039 | WGEN Man. oper. gen. lubrication | Generator | WGEN | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 41
2828 | 2040 | WGEN Timeout fault gen. lubrication | Generator | WGEN | Error | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 42
2831 | 2041 | WGEN Max. time generator bear.lubr. | Generator | WGEN | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 43
2832 | 2042 | WGEN Generator bearing lubr. container empty | Generator | WGEN | Warning | No |  |  | SCADA User | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 44
2900 | 2043 | WGEN Manual operation generator heating | Generator | WGEN | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 45
2910 | 2044 | WGEN Manual operation generator fan 1 | Generator | WGEN | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 46
2920 | 2045 | WGEN Manual operation generator fan 2 | Generator | WGEN | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 47
2930 | 2046 | WGEN Manual operation generator fan 3 | Generator | WGEN | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 48
2950 | 2047 | WGEN Lightning protection defect | Generator | WGEN | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 49
3390 | 2048 | WGEN Cool.sys. pump man.oper. | Generator | WGEN | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 50
3391 | 2049 | WGEN Heating coolant 1&2 man.oper. | Generator | WGEN | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 51
3392 | 2050 | WGEN Fans group 1&2 cool.sys. man.oper. | Generator | WGEN | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 52
3393 | 2051 | WGEN Heating fans 1-4 cool.sys. man.oper. | Generator | WGEN | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 53
2530 | 2200 | WGEN Gen. power derating act. | Protection | WGEN | Info | No |  | *5s | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 54
2829 | 2201 | WGEN Gen.lubr. self-protect. active | Protection | WGEN | Info | No |  | *5s | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 55
3155 | 2202 | WGEN Limit conv. output act.power | Protection | WGEN | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WGEN, row 56
86 | 3000 | WNAC 4-20mA outside temp. nacelle 1 | Meteorology | WNAC | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 2
87 | 3001 | WNAC 4-20mA outside temp. nacelle 2 | Meteorology | WNAC | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 3
88 | 3002 | WNAC Outs.temp. nacelle implaus. | Meteorology | WNAC | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 4
89 | 3003 | WNAC Nacelle outs/inside temp. comp. implausible | Meteorology | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 5
871 | 3004 | WNAC Light icing (rotor bl. ice sensor) | Meteorology | WNAC | Info | No | *20s | *5min | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 6
872 | 3005 | WNAC Icing (Rotor bl. ice sensor) | Meteorology | WNAC | Info | No |  | *5min | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 7
873 | 3006 | WNAC Icing (rotor bl. ice sens. no eval.) | Meteorology | WNAC | Info | No |  | *10min | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 8
874 | 3007 | WNAC Rotor blade ice sensor error | Meteorology | WNAC | Warning | No |  | *1min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 9
875 | 3008 | WNAC Rot.bl. ice sens. com. err. | Meteorology | WNAC | Info | Yes | *5min | *1min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 10
876 | 3009 | WNAC Rot.bl. ice s. eval. not pos. | Meteorology | WNAC | Info | Yes | *1h | *12min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 11
877 | 3010 | WNAC Rot.bl. ice sens. not ready | Meteorology | WNAC | Info | Yes | *5min | *1min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 12
878 | 3011 | WNAC Rotor blade ice sensor bypass active | Meteorology | WNAC | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 13
6501 | 3012 | WNAC Wind.sp. diff. level 1 | Meteorology | WNAC | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 14
6505 | 3013 | WNAC Wind.sp. diff. level 2 | Meteorology | WNAC | Error | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 15
6506 | 3014 | WNAC Dev. wind meas./est. | Meteorology | WNAC | Warning | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 16
6510 | 3015 | WNAC Anemometer 1 defect | Meteorology | WNAC | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 17
6512 | 3016 | WNAC Reboot anemometer 1 | Meteorology | WNAC | Warning | No |  |  | Operation Control | See only | See only | See only | See only | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 18
6515 | 3017 | WNAC 4-20mA anemometer 1 | Meteorology | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 19
6520 | 3018 | WNAC Anemometer 2 defect | Meteorology | WNAC | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 20
6522 | 3019 | WNAC Reboot anemometer 2 | Meteorology | WNAC | Warning | No |  |  | Operation Control | See only | See only | See only | See only | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 21
6525 | 3020 | WNAC 4-20mA anemometer 2 | Meteorology | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 22
6526 | 3021 | WNAC Anemometer 3 defect | Meteorology | WNAC | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 23
6527 | 3022 | WNAC 4-20mA anemometer 3 | Meteorology | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 24
6530 | 3023 | WNAC Anemometer defect | Meteorology | WNAC | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 25
6540 | 3024 | WNAC Icing (anemometer) | Meteorology | WNAC | Info | No |  | *3h | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 26
6541 | 3025 | WNAC No ice detection available | Meteorology | WNAC | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 27
6542 | 3026 | WNAC Reset of icing st. cd. possible | Meteorology | WNAC | Info | No | *1h |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Professional | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 28
6571 | 3027 | WNAC Ice anemometer de-icing | Meteorology | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 29
6601 | 3028 | WNAC Wind.dir. diff. level 1 | Meteorology | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 30
6605 | 3029 | WNAC Wind.dir. diff. level 2 | Meteorology | WNAC | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 31
6620 | 3030 | WNAC Vane defect | Meteorology | WNAC | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 32
6621 | 3031 | WNAC Vane 1 defect | Meteorology | WNAC | Warning | No | *3min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 33
6622 | 3032 | WNAC Vane 2 defect | Meteorology | WNAC | Warning | No | *3min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 34
6625 | 3033 | WNAC Check vane! | Meteorology | WNAC | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 35
6630 | 3034 | WNAC 4-20 mA vane 1 | Meteorology | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 36
6635 | 3035 | WNAC 4-20 mA vane 2 | Meteorology | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 37
6670 | 3036 | WNAC Light icing (red. operation) | Meteorology | WNAC | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 38
6680 | 3037 | WNAC Icing (red. operation) | Meteorology | WNAC | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 39
6681 | 3038 | WNAC Light icing (dev. electr. power) | Meteorology | WNAC | Info | No | *10min | *30min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 40
6682 | 3039 | WNAC Icing (dev. electr. power) | Meteorology | WNAC | Info | No | *10min | *30min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 41
6686 | 3040 | WNAC Extreme icing (wind > power) | Meteorology | WNAC | Warning | Yes | *30s |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 42
6690 | 3041 | WNAC Icing (stop) | Meteorology | WNAC | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 43
6694 | 3042 | WNAC Timed red. icing operation act. | Meteorology | WNAC | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 44
6695 | 3043 | WNAC Stop in case of ice det. act. | Meteorology | WNAC | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 45
6696 | 3044 | WNAC Test start during potential icing | Meteorology | WNAC | Info | No |  | *30min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 46
6697 | 3045 | WNAC Max. starts during icing | Meteorology | WNAC | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 47
6700 | 3046 | WNAC Shadow casting | Meteorology | WNAC | Info | No | *10s |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 48
6710 | 3047 | WNAC Shadow Management Unit defect | Meteorology | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 49
6711 | 3048 | WNAC Shadow Management Unit out of service | Meteorology | WNAC | Error | No | *10s |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 50
6712 | 3049 | WNAC Shadow Management Unit warning | Meteorology | WNAC | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 51
6720 | 3050 | WNAC Comm.err. IEC client -> Shadow Mgmt. Unit | Meteorology | WNAC | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 52
6721 | 3051 | WNAC Comm.err. IEC server -> Shadow Mgmt. Unit | Meteorology | WNAC | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 53
6750 | 3052 | WNAC Man. oper. meteorology heating | Meteorology | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 54
4000 | 3200 | WNAC High temperature nacelle | Nacelle | WNAC | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 55
4020 | 3201 | WNAC Max. temperature nacelle | Nacelle | WNAC | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 56
4024 | 3202 | WNAC 4-20mA inside temp. nacelle | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 57
4061 | 3203 | WNAC Rel. air hum. nacelle inside high (in operation) | Nacelle | WNAC | Warning | No | *90min |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 58
4062 | 3204 | WNAC Rel. air hum. nacelle inside too high (in operation) | Nacelle | WNAC | Error | No | *3h |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 59
4072 | 3205 | WNAC Rel. air hum. nacelle inside too high | Nacelle | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 60
4075 | 3206 | WNAC 4-20mA rel. air humidity nacelle int. | Nacelle | WNAC | Warning | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 61
4086 | 3207 | WNAC 4-20mA rel. air humidity tower base int. | Nacelle | WNAC | Warning | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 62
4091 | 3208 | WNAC Rel. air hum. tower base inside high (in operation) | Nacelle | WNAC | Warning | No | *90min |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 63
4092 | 3209 | WNAC Rel. air hum. tower base inside too high | Nacelle | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 64
4093 | 3210 | WNAC Rel. air hum. tower base inside too high (in operation) | Nacelle | WNAC | Error | No | *3h |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 65
4100 | 3211 | WNAC Vibration | Nacelle | WNAC | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 66
4150 | 3212 | WNAC Vibration sensor error | Nacelle | WNAC | Info | No | *1s |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 67
4200 | 3213 | WNAC Fault fire alarm system | Nacelle | WNAC | Error | No | *15s |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 68
4201 | 3214 | WNAC Fire warning | Nacelle | WNAC | Error | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 69
4202 | 3215 | WNAC Fire alarm | Nacelle | WNAC | Error | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 70
4203 | 3216 | WNAC Fire shut down | Nacelle | WNAC | Error | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 71
4204 | 3217 | WNAC Service fire alarm system | Nacelle | WNAC | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 72
4205 | 3218 | WNAC Fire alarm system inactive | Nacelle | WNAC | Error | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 73
4210 | 3219 | WNAC Smoke warning nacelle | Nacelle | WNAC | Warning | No | *5s |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 74
4215 | 3220 | WNAC Smoke warning nacelle stop | Nacelle | WNAC | Error | No | *5s |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 75
4220 | 3221 | WNAC Smoke warning tower base | Nacelle | WNAC | Warning | No | *5s |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 76
4225 | 3222 | WNAC Smoke warning tow. base stop | Nacelle | WNAC | Error | No | *5s |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 77
4230 | 3223 | WNAC Grid disc. smoke warning | Nacelle | WNAC | Error | No | *40s |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 78
4250 | 3224 | WNAC Manual operation nacelle fan | Nacelle | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 79
4252 | 3225 | WNAC Failure nacelle fan | Nacelle | WNAC | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 80
4253 | 3226 | WNAC Overload nacelle fan | Nacelle | WNAC | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 81
4255 | 3227 | WNAC Dry mode nacelle | Nacelle | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 82
4260 | 3228 | WNAC Manual operation rotor hub fan | Nacelle | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 83
4262 | 3229 | WNAC Failure rotor hub fan | Nacelle | WNAC | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 84
4263 | 3230 | WNAC Overload rotor hub fan | Nacelle | WNAC | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 85
4270 | 3231 | WNAC Manual operation cooling pump | Nacelle | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 86
4272 | 3232 | WNAC Failure cooling pump | Nacelle | WNAC | Warning | No | *5s |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 87
4273 | 3233 | WNAC Overload cooling pump | Nacelle | WNAC | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 88
4275 | 3234 | WNAC Pressure coolant nacelle high | Nacelle | WNAC | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 89
4276 | 3235 | WNAC Pressure difference cooling pump (nacelle) low | Nacelle | WNAC | Warning | No | *0 ms |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 90
4277 | 3236 | WNAC Coolant pump diff.press. (nacelle) too low | Nacelle | WNAC | Warning | No | *0 ms |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 91
4278 | 3237 | WNAC Coolant pump diff.press. (nacelle) high | Nacelle | WNAC | Warning | No | *0 ms |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 92
4279 | 3238 | WNAC Coolant pump diff.press. (nacelle) too high | Nacelle | WNAC | Warning | No | *0 ms |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 93
4280 | 3239 | WNAC Error meas. pressure coolant nacelle | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 94
4281 | 3240 | WNAC Signal Pressure coolant nacelle disturbed | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 95
4285 | 3241 | WNAC Error meas. coolant press. nacelle pump inlet | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 96
4286 | 3242 | WNAC Signal Pressure coolant nacelle pump inlet disturbed | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 97
4290 | 3243 | WNAC Error meas. temperature coolant nacelle cooler | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 98
4291 | 3244 | WNAC Signal Temperature coolant nacelle cooler disturbed | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 99
4293 | 3245 | WNAC Error meas. temperature coolant generator | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 100
4294 | 3246 | WNAC Signal Temperature coolant generator disturbed | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 101
4296 | 3247 | WNAC Error meas. temperature coolant gearbox | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 102
4297 | 3248 | WNAC Signal Temperature coolant gearbox disturbed | Nacelle | WNAC | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 103
4730 | 3249 | WNAC Drying mode tower base | Nacelle | WNAC | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WNAC, row 104
513 | 4000 | WROT Timeout bridging limit switches | Rotor | WROT | Error | No | *15s |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 2
515 | 4001 | WROT Pitch limit switches | Rotor | WROT | Error | No | *10s |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 3
516 | 4002 | WROT Pitch limit switch 1 | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 4
517 | 4003 | WROT Pitch limit switch 2 | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 5
518 | 4004 | WROT Pitch limit switch 3 | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 6
520 | 4005 | WROT Overload axis 1 | Rotor | WROT | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 7
525 | 4006 | WROT Overload axis 2 | Rotor | WROT | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 8
530 | 4007 | WROT Overload axis 3 | Rotor | WROT | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 9
550 | 4008 | WROT Pitch current asymmetry | Rotor | WROT | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 10
551 | 4009 | WROT Pitch motor current too high | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 11
553 | 4010 | WROT Blade pitch deviation test | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 12
555 | 4011 | WROT Pitch angle deviation | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 13
556 | 4012 | WROT Pitch deviation BP70 | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 14
558 | 4013 | WROT Pitch deviation Pitch Back | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 15
563 | 4014 | WROT 563 Pitch too fast during fast pitch back | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 16
564 | 4015 | WROT Bladeangle implausible | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 17
565 | 4016 | WROT Max. windspeed bladeangle | Rotor | WROT | Error | Yes | *0 ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 18
566 | 4017 | WROT Pitch too slow BP10 | Rotor | WROT | Error | No | *2s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 19
567 | 4018 | WROT Pitch too slow BP20 | Rotor | WROT | Error | No | *2s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 20
568 | 4019 | WROT Pitch too slow BP30 | Rotor | WROT | Error | No | *2s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 21
569 | 4020 | WROT Pitch too slow BP40 | Rotor | WROT | Error | No | *2s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 22
570 | 4021 | WROT Pitch too slow BP70 | Rotor | WROT | Error | No | *2s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 23
574 | 4022 | WROT Pitch too slow BP70 | Rotor | WROT | Error | No | *2s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 24
576 | 4023 | WROT Pitch too slow BP70 | Rotor | WROT | Error | No | *2s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 25
577 | 4024 | WROT Pitch too fast BP70 | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 26
578 | 4025 | WROT Pitch set point slow hold time BP40 | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 27
579 | 4026 | WROT Pitch too fast BP40 | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 28
581 | 4027 | WROT Set point><actual value axis 1 | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 29
582 | 4028 | WROT Set point><actual value axis 2 | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 30
583 | 4029 | WROT Set point><actual value axis 3 | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 31
588 | 4030 | WROT Target >< act. coll. pitch angle | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 32
592 | 4031 | WROT Great deviation blade pitches | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 33
594 | 4032 | WROT Blade pitch check running | Rotor | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 34
600 | 4033 | WROT Max. temp. motor axis 1 | Rotor | WROT | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 35
605 | 4034 | WROT Max. temp. motor axis 2 | Rotor | WROT | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 36
610 | 4035 | WROT Max. temp. motor axis 3 | Rotor | WROT | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 37
628 | 4036 | WROT Max. temp. pitch motor PTC | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 38
630 | 4037 | WROT 630 Overload fan pitch motor | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 39
641 | 4038 | WROT Sim.angle E enc. <> act.angle 1 | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 40
642 | 4039 | WROT Sim.angle E enc. <> act.angle 2 | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 41
643 | 4040 | WROT Sim.angle E enc. <> act.angle 3 | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 42
644 | 4041 | WROT Sim.angle D <> E enc. | Rotor | WROT | Info | Yes | *100ms |  | Department | See only | See only | See only | See only | Covert | See only | See only | [5 empty] | sales: 'See Only' written as 'See only'; tcc: 'See Only' written as 'See only'; service: 'See Only' written as 'See only'; turbine_operator_package: 'See Only' written as 'See only'; service_partner: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 43
650 | 4042 | WROT Pitch controller communication error | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 44
652 | 4043 | WROT Pitch controller initialisation error | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 45
656 | 4044 | WROT Error pitch converter 1 | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 46
657 | 4045 | WROT Error pitch converter 2 | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 47
658 | 4046 | WROT Error pitch converter 3 | Rotor | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 48
660 | 4047 | WROT Limit switches error 91° | Rotor | WROT | Error | No | *30s |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 49
664 | 4048 | WROT Pitch system temperature low | Rotor | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 50
665 | 4049 | WROT Pitch error | Rotor | WROT | Error | Yes |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 51
666 | 4050 | WROT Pitch box temp. too low | Rotor | WROT | Error | Yes |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 52
667 | 4051 | WROT Pitch box temp. implaus. | Rotor | WROT | Warning | Yes | *2min |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 53
668 | 4052 | WROT Battery boxes overtemp. | Rotor | WROT | Error | Yes |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 54
669 | 4053 | WROT Battery boxes heating sys. fault | Rotor | WROT | Error | Yes |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 55
670 | 4054 | WROT Max. pitch speed encoder A | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 56
672 | 4055 | WROT Max. pitch speed encoder B | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 57
675 | 4056 | WROT Pitch measuring system 1><2 | Rotor | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 58
679 | 4057 | WROT Pitch system temperature high | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 59
681 | 4058 | WROT Limit switch error 95° axis 1 | Rotor | WROT | Warning | No | *350ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 60
682 | 4059 | WROT Limit switch error 95° axis 2 | Rotor | WROT | Warning | No | *350ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 61
683 | 4060 | WROT Limit switch error 95° axis 3 | Rotor | WROT | Warning | No | *350ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 62
687 | 4061 | WROT Power failure pitch | Rotor | WROT | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 63
695 | 4062 | WROT Hub temperature high | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 64
697 | 4063 | WROT Timeout B sensor active | Rotor | WROT | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 65
700 | 4064 | WROT Batt. undervoltage/overvoltage | Rotor | WROT | Error | Yes | *30s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 66
707 | 4065 | WROT Stop battery test | Rotor | WROT | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 67
710 | 4066 | WROT Battery test | Rotor | WROT | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 68
711 | 4067 | WROT Battery monitoring axis 1 | Rotor | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 69
712 | 4068 | WROT Battery monitoring axis 2 | Rotor | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 70
713 | 4069 | WROT Battery monitoring axis 3 | Rotor | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 71
714 | 4070 | WROT Battery monitoring test interval | Rotor | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 72
715 | 4071 | WROT Charging circuit pitch | Rotor | WROT | Error | Yes | *1min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 73
716 | 4072 | WROT Battery charge cycle axis 1 error | Rotor | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 74
717 | 4073 | WROT Battery charge cycle axis 2 error | Rotor | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 75
718 | 4074 | WROT Battery charge cycle axis 3 error | Rotor | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 76
740 | 4075 | WROT Pitch back trigger by HC | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 77
741 | 4076 | WROT Battery drive trigger by HC | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 78
775 | 4077 | WROT Pitch heating mode | Rotor | WROT | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 79
776 | 4078 | WROT Timeout pitch heating mode | Rotor | WROT | Warning | No | *12h |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 80
780 | 4079 | WROT Error bridging start-up | Rotor | WROT | Error | No | *2500ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 81
785 | 4080 | WROT Error brake resistor CHP | Rotor | WROT | Warning | No | *2500ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 82
786 | 4081 | WROT Signal bridging start-up + CHP | Rotor | WROT | Warning | No | *2500ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 83
806 | 4082 | WROT High rotor speed hub | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 84
811 | 4083 | WROT Maximum rotor speed hub | Rotor | WROT | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 85
821 | 4084 | WROT Rotor rotation direction hub | Rotor | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 86
825 | 4085 | WROT Rotor speed hub<>gear.sp. | Rotor | WROT | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 87
826 | 4086 | WROT Rotor speed hub<<>>gear.sp. | Rotor | WROT | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 88
829 | 4087 | WROT Rotor speed SLC<>gear.sp. | Rotor | WROT | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 89
830 | 4088 | WROT Calc. rotor position implausible | Rotor | WROT | Warning | No |  | *5min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 90
831 | 4089 | WROT Rotor position diff. | Rotor | WROT | Error | Yes | *5s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 91
835 | 4090 | WROT Check determ. of rotor position | Rotor | WROT | Warning | No |  | *5min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 92
836 | 4091 | WROT Rotor pos. change not plausible | Rotor | WROT | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 93
850 | 4092 | WROT Error lubrication pump pitch | Rotor | WROT | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 94
855 | 4093 | WROT Stop after blade bear.lubr.dr. BP10 | Rotor | WROT | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 95
856 | 4094 | WROT Stop after blade bear.lubr.dr. 90° | Rotor | WROT | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 96
857 | 4095 | WROT Blade bear.lubr.dr. timeout | Rotor | WROT | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 97
858 | 4096 | WROT Blade bear.lubr. failure | Rotor | WROT | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 98
15000 | 4200 | WROT Hot air de-icing positioning | Hot Air De-icing | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 99
15001 | 4201 | WROT Ending hot air de-icing | Hot Air De-icing | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 100
15003 | 4202 | WROT HAD man. ice prevention | Hot Air De-icing | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 101
15004 | 4203 | WROT HAD ice prevention | Hot Air De-icing | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 102
15005 | 4204 | WROT Hot air de-icing active | Hot Air De-icing | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 103
15010 | 4205 | WROT HAD semi-aut. op. | Hot Air De-icing | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 104
15015 | 4206 | WROT HAD motor prot. fan OFF | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 105
15016 | 4207 | WROT HAD motor prot. heat.reg. OFF | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 106
15021 | 4208 | WROT HAD motor prot. heat.reg. A1 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 107
15022 | 4209 | WROT HAD motor prot. heat.reg. A2 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 108
15023 | 4210 | WROT HAD motor prot. heat.reg. A3 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 109
15040 | 4211 | WROT HAD outside temp. de-icing too high | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 110
15041 | 4212 | WROT HAD outside temp. de-icing too low | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 111
15042 | 4213 | WROT HAD outside temp. ice prev. too high | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 112
15043 | 4214 | WROT HAD outside temp. ice prev. too low | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 113
15050 | 4215 | WROT HAD overtemp. relay | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 114
15055 | 4216 | WROT HAD overtemp. flow | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 115
15056 | 4217 | WROT HAD overtemp. control box | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 116
15060 | 4218 | WROT HAD overtemp. heating | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 117
15062 | 4219 | WROT HAD temp. sensor drift A1 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 118
15063 | 4220 | WROT HAD temp. sensor drift A2 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 119
15064 | 4221 | WROT HAD temp. sensor drift A3 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 120
15065 | 4222 | WROT HAD temp. sensor error | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 121
15068 | 4223 | WROT HAD rotor pos. sensor error | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 122
15071 | 4224 | WROT HAD error HFU contact. A1 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 123
15072 | 4225 | WROT HAD error HFU contact. A2 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 124
15073 | 4226 | WROT HAD error HFU contact. A3 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 125
15078 | 4227 | WROT HAD error overtemp. Relay | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 126
15081 | 4228 | WROT HAD motor prot. fan A1 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 127
15082 | 4229 | WROT HAD motor prot. fan A2 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 128
15083 | 4230 | WROT HAD motor prot. fan A3 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 129
15085 | 4231 | WROT HAD de-icing implausible | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 130
15090 | 4232 | WROT HAD communication error | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 131
15091 | 4233 | WROT HAD comm.version error | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 132
15094 | 4234 | WROT HAD rotor pos. implausible | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 133
15095 | 4235 | WROT HAD timeout positioning | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 134
15096 | 4236 | WROT HAD timeout de-icing A1 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 135
15097 | 4237 | WROT HAD timeout de-icing A2 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 136
15098 | 4238 | WROT HAD timeout de-icing A3 | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 137
15101 | 4239 | WROT HAD max. CPU temp. | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 138
15102 | 4240 | WROT HAD CPU error RTC | Hot Air De-icing | WROT | Warning | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 139
15103 | 4241 | WROT HAD CPU NVRAM battery | Hot Air De-icing | WROT | Warning | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 140
15104 | 4242 | WROT HAD CPU memory error | Hot Air De-icing | WROT | Warning | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 141
15105 | 4243 | WROT HAD division by zero | Hot Air De-icing | WROT | Warning | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | See only | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 142
15106 | 4244 | WROT HAD prog.runtime error 10ms | Hot Air De-icing | WROT | Warning | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | See only | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 143
15107 | 4245 | WROT HAD mconfig.ini check failed | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 144
15115 | 4246 | WROT HAD PLC hardware error | Hot Air De-icing | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 145
5000 | 4300 | WROT Breakdown obstacle light | Lighting | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 146
5001 | 4301 | WROT Breakdown low intensity obstacle light | Lighting | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 147
5020 | 4302 | WROT Failure visibility measuring | Lighting | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 148
5025 | 4303 | WROT Error no. visibility meas. devices | Lighting | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 149
5100 | 4304 | WROT Service obstacle light | Lighting | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 150
653 | 4400 | WROT Blade load sensors comm.failure | Blade Sensors | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 151
654 | 4401 | WROT Blade load sensors firmware error | Blade Sensors | WROT | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 152
960 | 4402 | WROT Blade load sensors not RFO | Blade Sensors | WROT | Warning | Yes | *1s |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 153
961 | 4403 | WROT Blade load sensors zero offset indiv. error | Blade Sensors | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 154
962 | 4404 | WROT Blade load sensors gain error | Blade Sensors | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only'; set delay in the source: '*' (not a time; left empty) | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 155
963 | 4405 | WROT Blade load sensors homog. error | Blade Sensors | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only'; set delay in the source: '*' (not a time; left empty) | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 156
964 | 4406 | WROT Blade load sensors strain diff. high | Blade Sensors | WROT | Warning | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only'; set delay in the source: '*' (not a time; left empty) | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 157
965 | 4407 | WROT Blade load sensors implaus.meas.val. | Blade Sensors | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 158
967 | 4408 | WROT Blade load sensors signal check | Blade Sensors | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 159
968 | 4409 | WROT Blade load sensors signal check error | Blade Sensors | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 160
969 | 4410 | WROT Rotor blade load sensor back-up mode | Blade Sensors | WROT | Warning | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only'; set delay in the source: '*' (not a time; left empty); reset delay in the source: '*' (not a time; left empty) | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 161
970 | 4411 | WROT Alarm - cont. blade load sensors back-up mode | Blade Sensors | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only'; set delay in the source: '*' (not a time; left empty) | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 162
971 | 4412 | WROT Stop - blade load sensors back-up mode | Blade Sensors | WROT | Info | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 163
972 | 4413 | WROT Blade load sensors no signal activity | Blade Sensors | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 164
973 | 4414 | WROT Check blade bend.mom. | Blade Sensors | WROT | Info | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 165
974 | 4415 | WROT Blade load sensors zero offset error | Blade Sensors | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WROT, row 166
4500 | 5000 | WTOW Tower resonance | Tower | WTOW | Info | No | *1min |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 2
4502 | 5001 | WTOW Nat. tower freq. implausible | Tower | WTOW | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 3
4503 | 5002 | WTOW Nat. tower freq. calc. imp. | Tower | WTOW | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 4
4510 | 5003 | WTOW Tower oscillation Y level 1 | Tower | WTOW | Info | Yes | *0 ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 5
4511 | 5004 | WTOW Tower oscillation Y level 1 standst. | Tower | WTOW | Info | Yes | *0 ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 6
4520 | 5005 | WTOW Tower oscillation X level 1 | Tower | WTOW | Info | Yes | *0 ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 7
4521 | 5006 | WTOW Tower oscillation X level 1 standst. | Tower | WTOW | Info | Yes | *0 ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 8
4530 | 5007 | WTOW Tower oscillation Y level 2 | Tower | WTOW | Info | Yes | *3s | *15min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 9
4531 | 5008 | WTOW Tower oscillation Y level 2 standst. | Tower | WTOW | Info | Yes | *3s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 10
4535 | 5009 | WTOW Tower oscillation Y level 3 | Tower | WTOW | Error | Yes | *150ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 11
4540 | 5010 | WTOW Tower oscillation X level 2 | Tower | WTOW | Info | Yes | *3s | *15min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 12
4541 | 5011 | WTOW Tower oscillation X level 2 standst. | Tower | WTOW | Info | Yes | *3s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 13
4545 | 5012 | WTOW Tower oscillation X level 3 | Tower | WTOW | Error | Yes | *150ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 14
4555 | 5013 | WTOW Tower accel. difference | Tower | WTOW | Error | Yes | *0 ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 15
4565 | 5014 | WTOW System fault accel. sensor 1 | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 16
4582 | 5015 | WTOW Oscil.sensor 1: check firmware | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 17
4583 | 5016 | WTOW Oscil.sensor 2: check firmware | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 18
4584 | 5017 | WTOW Oscill. encoder tower (BP act.) | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 19
4585 | 5018 | WTOW 4-20mA tower acceleration Y | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 20
4587 | 5019 | WTOW 4-20mA tower acceleration X | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 21
4588 | 5020 | WTOW Oscillation encoder tower | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 22
4589 | 5021 | WTOW Oscillation encoder TwC | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 23
4600 | 5022 | WTOW PT100 base box temp. defect | Tower | WTOW | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 24
4603 | 5023 | WTOW Base box temperature high | Tower | WTOW | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 25
4604 | 5024 | WTOW Base box temperature low | Tower | WTOW | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 26
4605 | 5025 | WTOW Error measuring temp. tower base box | Tower | WTOW | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 27
4607 | 5026 | WTOW Heating/fan base box faulty | Tower | WTOW | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 28
4608 | 5027 | WTOW Tower distrib. cabinet def. | Tower | WTOW | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 29
4609 | 5028 | WTOW Max. base box temp. | Tower | WTOW | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 30
4611 | 5029 | WTOW PT100 temp. tower base defective | Tower | WTOW | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 31
4645 | 5030 | WTOW 4-20mA tower accel. Y2 (TwC) | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 32
4647 | 5031 | WTOW 4-20mA tower accel. X2 (TwC) | Tower | WTOW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 33
4700 | 5032 | WTOW Failure tower fan | Tower | WTOW | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 34
4710 | 5033 | WTOW Manual operation tower fan | Tower | WTOW | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 35
4720 | 5034 | WTOW Tower fan overload | Tower | WTOW | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 36
4800 | 5035 | WTOW Persons in the tower base | Tower | WTOW | Warning | No | *3s |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 37
4810 | 5036 | WTOW Tower door opened | Tower | WTOW | Warning | No | *3s |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 38
4951 | 5037 | WTOW Accel.sensor XF/YF comm.error | Tower | WTOW | Warning | No | *5s |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 39
4956 | 5038 | WTOW Accel.sensor XF/YF system error | Tower | WTOW | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 40
4960 | 5039 | WTOW Tower oscillation YF | Tower | WTOW | Info | No | *100ms | *15min | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 41
4970 | 5040 | WTOW Tower oscillation XF | Tower | WTOW | Info | No | *100ms | *15min | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 42
6640 | 5041 | WTOW 4-20mA tower base outsidetemp. | Tower | WTOW | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 43
6642 | 5042 | WTOW 4-20mA tower base outsidetemp. | Tower | WTOW | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTOW, row 44
3804 | 6000 | WTRF MVS Trafo CB tripped | Switches | WTRF | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 2
3807 | 6001 | WTRF MVS Trafo CB remote off | Switches | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 3
9801 | 6002 | WTRF MVS grid disconn. off | Switches | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 4
9802 | 6003 | WTRF MVS grid ES on | Switches | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 5
9811 | 6004 | WTRF MVS cable outlet 1 disconn. off | Switches | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 6
9812 | 6005 | WTRF MVS cable outlet 1 ES on | Switches | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 7
9821 | 6006 | WTRF MVS cable outlet 2 disconn. off | Switches | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 8
9822 | 6007 | WTRF MVS cable outlet 2 ES on | Switches | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 9
3800 | 6200 | WTRF Circuit breaker | Transformer | WTRF | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 10
3802 | 6201 | WTRF MVS Trafo CB off | Transformer | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 11
3803 | 6202 | WTRF P reduction current limitation | Transformer | WTRF | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 12
3805 | 6203 | WTRF Max. transformer temp. | Transformer | WTRF | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 13
3809 | 6204 | WTRF P reduction apparent power limitation | Transformer | WTRF | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 14
3810 | 6205 | WTRF Medium voltage off | Transformer | WTRF | Error | No | *30MIN |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 15
3812 | 6206 | WTRF MVS Transf. Disc. off | Transformer | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 16
3814 | 6207 | WTRF MVS Transf. ES on | Transformer | WTRF | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 17
3836 | 6208 | WTRF MSS Protection system error | Transformer | WTRF | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 18
3840 | 6209 | WTRF SF6 boiler pressure too low | Transformer | WTRF | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 19
3849 | 6210 | WTRF Spare potection inactive | Transformer | WTRF | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 20
3892 | 6211 | WTRF PT100 transf. int. defect. | Transformer | WTRF | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 21
3894 | 6212 | WTRF Error meas. temp. transf.int. | Transformer | WTRF | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 22
3904 | 6213 | WTRF Max. temp. supply transformer | Transformer | WTRF | Error | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 23
3907 | 6214 | WTRF Max. temp. supply transf. grid disconn. | Transformer | WTRF | Error | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | set delay in the source: '*' (not a time; left empty) | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 24
3912 | 6215 | WTRF Transf. oil pressure too high | Transformer | WTRF | Error | No | *100ms | *100ms | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 25
3914 | 6216 | WTRF Transf. fill level too low | Transformer | WTRF | Error | No | *100ms | *100ms | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 26
3942 | 6217 | WTRF PT100 supply transformer def. | Transformer | WTRF | Error | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 27
3943 | 6218 | WTRF Error measuring PT100 supply transf. | Transformer | WTRF | Error | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 28
3950 | 6219 | WTRF Aux. power operation error | Transformer | WTRF | Error | No | *1s | *5s | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 29
3954 | 6220 | WTRF Max. overv. aux. power ctrl. | Transformer | WTRF | Error | No | *1s | *0 ms | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 30
3960 | 6221 | WTRF Max. temp. aux. transf. nacelle | Transformer | WTRF | Error | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 31
3962 | 6222 | WTRF PT100 aux. transformer nacelle def. | Transformer | WTRF | Error | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 32
3963 | 6223 | WTRF Error meas. nacelle aux. transf. | Transformer | WTRF | Error | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 33
3970 | 6224 | WTRF Transformer pump overload | Transformer | WTRF | Warning | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 34
3972 | 6225 | WTRF Transf. pump thermist. tripped | Transformer | WTRF | Warning | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 35
3974 | 6226 | WTRF Transf. pump man.oper. | Transformer | WTRF | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRF, row 36
1500 | 7000 | WTRM High gearbox oil pressure | Gearbox | WTRM | Error | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 2
1510 | 7001 | WTRM Low gearbox oil pressure | Gearbox | WTRM | Error | No | *1min |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 3
1520 | 7002 | WTRM 4-20mA press. gearbox pump | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 4
1525 | 7003 | WTRM 4-20mA press. gearbox inlet | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 5
1530 | 7004 | WTRM Error measuring pressure inlet gear | Gearbox | WTRM | Warning | No | *2min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 6
1548 | 7005 | WTRM Missing gear oil (low rpm) | Gearbox | WTRM | Error | No | *1min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 7
1550 | 7006 | WTRM Missing gear oil (high rpm) | Gearbox | WTRM | Error | No | *1min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 8
1552 | 7007 | WTRM Gearbox warm-up stage | Gearbox | WTRM | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 9
1555 | 7008 | WTRM Gear heating enabled | Gearbox | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 10
1557 | 7009 | WTRM Gearbox warmed up idling | Gearbox | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 11
1558 | 7010 | WTRM Timeout gearoil heating routine active | Gearbox | WTRM | Warning | No | *6h |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 12
1560 | 7011 | WTRM Manual operation fan gear | Gearbox | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 13
1565 | 7012 | WTRM Manual operation gear heating | Gearbox | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 14
1570 | 7013 | WTRM Manual operation gear oil pump | Gearbox | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 15
1600 | 7014 | WTRM High gear speed | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 16
1610 | 7015 | WTRM Maximum gear speed | Gearbox | WTRM | Error | Yes | *55ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 17
1625 | 7016 | WTRM Implausible gear speed leap | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 18
1630 | 7017 | WTRM Disc filter adaption implausible | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 19
1680 | 7018 | WTRM Gearb.sp. SLC <> gearb.sp. | Gearbox | WTRM | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 20
1685 | 7019 | WTRM Gear ratio param. implaus. | Gearbox | WTRM | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 21
1700 | 7020 | WTRM High temp. gear bearing 1 | Gearbox | WTRM | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 22
1705 | 7021 | WTRM Max. temp. gear bearing 1 | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 23
1707 | 7022 | WTRM PT100 gear bearing 1 defect | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 24
1708 | 7023 | WTRM Error measuring temp. gear bearing 1 | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 25
1710 | 7024 | WTRM High temp. gear bearing 2 | Gearbox | WTRM | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 26
1715 | 7025 | WTRM Max. temp. gear bearing 2 | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 27
1717 | 7026 | WTRM PT100 gear bearing 2 defect | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 28
1718 | 7027 | WTRM Error measuring temp. gear bearing 2 | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 29
1720 | 7028 | WTRM Max. oilsump temperature | Gearbox | WTRM | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 30
1723 | 7029 | WTRM Oilsump temperature high | Gearbox | WTRM | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 31
1725 | 7030 | WTRM Low gear oil temperature | Gearbox | WTRM | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 32
1727 | 7031 | WTRM PT100 gear oil sump defect | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 33
1728 | 7032 | WTRM Error measuring temp. gear oil sump | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 34
1729 | 7033 | WTRM PT100 inlet gear defect | Gearbox | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 35
1731 | 7034 | WTRM Oil temperature gearbox input high | Gearbox | WTRM | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 36
1732 | 7035 | WTRM Max. oil temperature gearbox input | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 37
1738 | 7036 | WTRM Error measuring temp. inlet gear | Gearbox | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 38
1740 | 7037 | WTRM High temp. gear bearing 3 | Gearbox | WTRM | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 39
1745 | 7038 | WTRM Max. temp. gear bearing 3 | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 40
1747 | 7039 | WTRM PT100 gear bearing 3 defect | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 41
1748 | 7040 | WTRM Error measuring temp. gear bearing 3 | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 42
1750 | 7041 | WTRM High temp. gear bearing 4 | Gearbox | WTRM | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 43
1755 | 7042 | WTRM Max. temp. gear bearing 4 | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 44
1757 | 7043 | WTRM PT100 gear bearing 4 defect | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 45
1758 | 7044 | WTRM Error measuring temp. gear bearing 4 | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 46
1800 | 7045 | WTRM Overload gear oil pump | Gearbox | WTRM | Error | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 47
1810 | 7046 | WTRM Overload gear heating | Gearbox | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 48
1816 | 7047 | WTRM Fault fan gear oil cooler 1 | Gearbox | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 49
1818 | 7048 | WTRM Overload fan 1 gear oil cooler | Gearbox | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 50
1819 | 7049 | WTRM Overload fan 2 gear oil cooler | Gearbox | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 51
1822 | 7050 | WTRM Fault fan gear oil cooler 2 | Gearbox | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 52
1824 | 7051 | WTRM Fault fan gear oil cooler 1+2 | Gearbox | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 53
1860 | 7052 | WTRM Oil filter gear choked | Gearbox | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 54
1870 | 7053 | WTRM 4-20mA pressure diff. gear oil filter | Gearbox | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 55
1880 | 7054 | WTRM Error meas. press. diff. oil filter | Gearbox | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 56
1920 | 7055 | WTRM Particle sensor defect | Gearbox | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 57
1922 | 7056 | WTRM Particle Gear Alarm 10min | Gearbox | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 58
1924 | 7057 | WTRM Particle Gear Alarm 24h | Gearbox | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 59
1926 | 7058 | WTRM Particle Gear Alarm Total | Gearbox | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 60
1001 | 7200 | WTRM Drive train oscillation Z level 0 | Drive train | WTRM | Warning | No |  |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 61
1005 | 7201 | WTRM Drive train oscillation Z level 1 | Drive train | WTRM | Error | Yes | *10s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 62
1015 | 7202 | WTRM Drive train oscillation Z level 2 | Drive train | WTRM | Error | Yes | *5s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 63
1050 | 7203 | WTRM Drivetrain oscillations | Drive train | WTRM | Warning | No |  | *2s | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 64
1055 | 7204 | WTRM Max. drivetrain oscillations | Drive train | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 65
1065 | 7205 | WTRM Drive train monitor level 1 | Drive train | WTRM | Info | No | *1min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 66
1070 | 7206 | WTRM Drive train monitor level 2 | Drive train | WTRM | Info | No | *5s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 67
1125 | 7207 | WTRM 4-20mA drive train acceleration Z | Drive train | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 68
1130 | 7208 | WTRM Acceleration detector drivetrain | Drive train | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 69
1150 | 7209 | WTRM CMS drive train system error | Drive train | WTRM | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 70
1151 | 7210 | WTRM CMS drive train meas. val. ev. | Drive train | WTRM | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 71
1160 | 7211 | WTRM Comm.err. IEC client -> CMS drive tr. | Drive train | WTRM | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 72
1161 | 7212 | WTRM Comm.err. IEC server <- CMS drive tr. | Drive train | WTRM | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 73
1200 | 7213 | WTRM High temp. rotorbearing | Drive train | WTRM | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 74
1210 | 7214 | WTRM Max. temp. rotorbearing | Drive train | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 75
1215 | 7215 | WTRM 4-20mA rotor bear. temp. | Drive train | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 76
1216 | 7216 | WTRM 4-20mA rotor bear. temp. timeout | Drive train | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 77
1311 | 7217 | WTRM Rotor bearing lubrication pump 1 overload | Drive train | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 78
1312 | 7218 | WTRM Rotor bearing lubrication pump 2 overload | Drive train | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 79
1313 | 7219 | WTRM Rotor bear. lubr.cont. 1 empty | Drive train | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 80
1314 | 7220 | WTRM Rotor bear. lubr.cont. 2 empty | Drive train | WTRM | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 81
1316 | 7221 | WTRM Timeout fault rotor bear. lubr. | Drive train | WTRM | Error | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 82
1319 | 7222 | WTRM Rotor bearing lubrication failure | Drive train | WTRM | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 83
1320 | 7223 | WTRM Rotor bearing lubric. man.op. | Drive train | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 84
1321 | 7224 | WTRM Max. time rotor bear.lubr. 1 | Drive train | WTRM | Warning | No | *5s |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 85
1322 | 7225 | WTRM Max. time rotor bear.lubr. 2 | Drive train | WTRM | Warning | No | *5s |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 86
1405 | 7226 | WTRM Rotor locked: Stop | Drive train | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 87
1407 | 7227 | WTRM Rotor lock - wind too strong | Drive train | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 88
1408 | 7228 | WTRM Rotor lock 1 on | Drive train | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 89
1409 | 7229 | WTRM Rotor lock 2 on | Drive train | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 90
1410 | 7230 | WTRM Rotor lock - no storm position | Drive train | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 91
5500 | 7300 | WTRM High hydraulic pressure | Hydraulics | WTRM | Error | No | *4s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 92
5505 | 7301 | WTRM High hydr. press. flush. mode | Hydraulics | WTRM | Warning | No | *100ms |  | Department | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 93
5506 | 7302 | WTRM Rot.br. press. high | Hydraulics | WTRM | Error | Yes | *200ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 94
5507 | 7303 | WTRM Max. rot.br. press. | Hydraulics | WTRM | Error | Yes | *100ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 95
5510 | 7304 | WTRM Low hydraulic pressure | Hydraulics | WTRM | Error | No | *4s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 96
5516 | 7305 | WTRM Rot.br. press. low | Hydraulics | WTRM | Error | Yes | *200ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 97
5517 | 7306 | WTRM Drain valve (MVB) test fail | Hydraulics | WTRM | Error | Yes | *200ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 98
5520 | 7307 | WTRM 4-20mA hydraulic pressure | Hydraulics | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 99
5525 | 7308 | WTRM 4-20mA rot.br. press. | Hydraulics | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 100
5550 | 7309 | WTRM Low hydraulic oil level | Hydraulics | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 101
5600 | 7310 | WTRM Overload hydraulic pump | Hydraulics | WTRM | Error | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 102
5700 | 7311 | WTRM Max. operation time hydraulic | Hydraulics | WTRM | Error | No | *30s |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 103
5710 | 7312 | WTRM Min. operation time hydraulic | Hydraulics | WTRM | Error | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 104
5730 | 7313 | WTRM Pressure drop hydraulic sys. | Hydraulics | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 105
5750 | 7314 | WTRM Manual operation hydraulic pump | Hydraulics | WTRM | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 106
5760 | 7315 | WTRM Hydraulic oil flushing operation | Hydraulics | WTRM | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 107
5770 | 7316 | WTRM Manual op. hydr. oil flushing | Hydraulics | WTRM | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 108
2005 | 7400 | WTRM Check brake | Brake | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 109
2007 | 7401 | WTRM Brake pads warning | Brake | WTRM | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 110
2050 | 7402 | WTRM Brake closed in operation | Brake | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 111
2125 | 7403 | WTRM Timeout brake closed | Brake | WTRM | Warning | Yes | *1s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 112
2150 | 7404 | WTRM Impulse braking | Brake | WTRM | Info | No |  | *1min | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 113
2160 | 7405 | WTRM Permanent braking | Brake | WTRM | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 114
2170 | 7406 | WTRM Additional braking | Brake | WTRM | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 115
2200 | 7407 | WTRM Max. braking energy exceeded | Brake | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 116
2340 | 7408 | WTRM Temp. rot.br.pad implaus. | Brake | WTRM | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 117
2350 | 7409 | WTRM Disc brake cooling down | Brake | WTRM | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 118
2355 | 7410 | WTRM Temp. rot.br.pad high | Brake | WTRM | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 119
2356 | 7411 | WTRM Max rot.br.pad temp. exceed. | Brake | WTRM | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 120
2357 | 7412 | WTRM Dragging brake monitoring | Brake | WTRM | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 121
2358 | 7413 | WTRM Temp. rot.br.pad high timeout | Brake | WTRM | Warning | Yes | *10min |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 122
2360 | 7414 | WTRM Error measuring temp. rot.br.pad 1 | Brake | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 123
2361 | 7415 | WTRM PT100 rot.br.pad 1 defect | Brake | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 124
2370 | 7416 | WTRM Error measuring temp. rot.br.pad 2 | Brake | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 125
2371 | 7417 | WTRM PT100 rot.br.pad 2 defect | Brake | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 126
2380 | 7418 | WTRM 0-10V error volt.buffer rot.br. | Brake | WTRM | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 127
2390 | 7419 | WTRM Brake due to sudden sys.failure | Brake | WTRM | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTRM, row 128
6000 | 8000 | WYAW Overload electr. yaw brake | Yaw | WYAW | Error | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 2
6007 | 8001 | WYAW Overload yaw motors group 1 | Yaw | WYAW | Error | No |  | *0 ms | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 3
6012 | 8002 | WYAW Overload yaw motors group 2 | Yaw | WYAW | Error | No |  | *0 ms | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 4
6039 | 8003 | WYAW Max. time yaw bear.lubr. | Yaw | WYAW | Warning | No | *5s |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 5
6040 | 8004 | WYAW Overload yaw lubr. Pump | Yaw | WYAW | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 6
6041 | 8005 | WYAW Yaw bearing lubric. man.op. | Yaw | WYAW | Info | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 7
6043 | 8006 | WYAW Timeout fault yaw lubrication | Yaw | WYAW | Error | No |  |  | SCADA User | Sales | Telenotdienst-read | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 8
6046 | 8007 | WYAW Error yaw lubr. pump (no ext. press. build-up) | Yaw | WYAW | Warning | No | *1s |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 9
6047 | 8008 | WYAW Error yaw lubr. pump (no ext. press. red.) | Yaw | WYAW | Warning | No | *1s |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 10
6048 | 8009 | WYAW Yaw lubr. container empty | Yaw | WYAW | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 11
6052 | 8010 | WYAW High yaw motor current | Yaw | WYAW | Info | No |  | *0 ms | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 12
6054 | 8011 | WYAW Easy yaw | Yaw | WYAW | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 13
6056 | 8012 | WYAW High yaw load | Yaw | WYAW | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 14
6100 | 8013 | WYAW Rotating direction yaw | Yaw | WYAW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 15
6111 | 8014 | WYAW Yaw velocity too low | Yaw | WYAW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 16
6115 | 8015 | WYAW Yaw sensor A defect | Yaw | WYAW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 17
6116 | 8016 | WYAW Yaw sensor B defect | Yaw | WYAW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 18
6120 | 8017 | WYAW Uncontrolled yaw movement | Yaw | WYAW | Error | No | *50ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 19
6130 | 8018 | WYAW Yaw speed high | Yaw | WYAW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 20
6200 | 8019 | WYAW Cable autounwind | Yaw | WYAW | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 21
6210 | 8020 | WYAW Max. cable twistangle | Yaw | WYAW | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 22
6300 | 8021 | WYAW Yaw error | Yaw | WYAW | Error | Yes |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Professional | [5 empty] | customer: 'ProfessionaProfessional' written as 'Professional' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 23
6350 | 8022 | WYAW Check nacelle position! | Yaw | WYAW | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 24
6355 | 8023 | WYAW Error nacelle pos. Load Man. | Yaw | WYAW | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 25
6356 | 8024 | WYAW Untwisting sensor test | Yaw | WYAW | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 26
6357 | 8025 | WYAW Nacelle position sensor fault | Yaw | WYAW | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 27
6400 | 8026 | WYAW Manual yaw brake | Yaw | WYAW | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 28
6410 | 8027 | WYAW Manual yaw | Yaw | WYAW | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 29
6411 | 8028 | WYAW Manual yaw via pushbutton | Yaw | WYAW | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 30
6412 | 8029 | WYAW Tower referencing act. | Yaw | WYAW | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 31
6430 | 8030 | WYAW Yaw current par. implausible | Yaw | WYAW | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 32
6432 | 8031 | WYAW 4-20mA yaw current sensor | Yaw | WYAW | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 33
6460 | 8032 | WYAW Yaw park pos. in case of icing | Yaw | WYAW | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WYAW, row 34
0 | 9001 | WTUR System OK | System | WTUR | Info | No |  |  | See only | See only | See only | See only | Covert | Covert | See only | See only | [5 empty] | development: 'See Only' written as 'See only'; sales: 'See Only' written as 'See only'; tcc: 'See Only' written as 'See only'; service: 'See Only' written as 'See only'; service_partner: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 2
10 | 9002 | WTUR Negative power, too little wind | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 3
11 | 9003 | WTUR Negative power, too little wind with icing | System | WTUR | Info | Yes |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 4
16 | 9004 | WTUR Timeout start for icing | System | WTUR | Info | No | *12min |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 5
20 | 9005 | WTUR Manual stop - on site | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 6
21 | 9006 | WTUR Manual stop - remote | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 7
25 | 9007 | WTUR Manual stop without login | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 8
28 | 9008 | WTUR WTG stop | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Standard | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 9
30 | 9009 | WTUR Wind sector stop | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Covert | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 10
45 | 9010 | WTUR Limiting wind speed exceeded | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 11
46 | 9011 | WTUR Max. wind dir. deviation high wind sp. | System | WTUR | Error | No | *5s |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 12
47 | 9012 | WTUR Max. windspeed BP10 | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 13
50 | 9013 | WTUR Night operation | System | WTUR | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 14
53 | 9014 | WTUR Wind dir.dev. level 1 | System | WTUR | Error | No | *5s |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 15
54 | 9015 | WTUR WTG shutdown - pitch angle & stormp. ignored | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 16
55 | 9016 | WTUR WTG shut down | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 17
57 | 9017 | WTUR Reduced power active | System | WTUR | Info | No | *0 ms | *0 ms | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Standard | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 18
58 | 9018 | WTUR Wind dir.dev. level 2 | System | WTUR | Error | No | *0 ms | *2min | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 19
59 | 9019 | WTUR Max. acceleration | System | WTUR | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 20
60 | 9020 | WTUR Wind > power | System | WTUR | Error | Yes | *30s |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 21
61 | 9021 | WTUR Wind < power | System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 22
62 | 9022 | WTUR Extreme gust | System | WTUR | Info | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 23
64 | 9023 | WTUR Max. wind speed | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 24
65 | 9024 | WTUR Absence of wind during run-up | System | WTUR | Info | No | *12min |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 25
70 | 9025 | WTUR Icing (nacelle ice sensor) | System | WTUR | Info | No |  | *3h | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 26
71 | 9026 | WTUR Outdoor temperature low | System | WTUR | Info | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 27
72 | 9027 | WTUR Outdoor temperature high | System | WTUR | Info | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 28
75 | 9028 | WTUR Reduced power gearbox | System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 29
76 | 9029 | WTUR Reduced power generator | System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 30
77 | 9030 | WTUR Reduced power transformer | System | WTUR | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 31
81 | 9031 | WTUR Outdoor temp. extremely low | System | WTUR | Warning | No |  | *2min | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 32
85 | 9032 | WTUR Outdoor temp.>working range | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 33
110 | 9033 | WTUR Emergency stop top box | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 34
111 | 9034 | WTUR Emergency stop nacelle | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 35
115 | 9035 | WTUR Emergency stop converter | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 36
117 | 9036 | WTUR Emergency stop base box | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 37
120 | 9037 | WTUR Conv. emergency stop 2 | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 38
121 | 9038 | WTUR Emer.stop tower base | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 39
200 | 9039 | WTUR Release manual pitch | System | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 40
201 | 9040 | WTUR Manual pitch active | System | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 41
205 | 9041 | WTUR Pitch service mode | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 42
210 | 9042 | WTUR Manual brake | System | WTUR | Info | Yes |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [5 empty] | sales: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 43
220 | 9043 | WTUR Sound characteristic A active | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 44
221 | 9044 | WTUR Sound characteristic C active | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 45
225 | 9045 | WTUR Sound characteristic B active | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 46
226 | 9046 | WTUR Sound characteristic D active | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 47
228 | 9047 | WTUR Noise reduction stop | System | WTUR | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 48
229 | 9048 | WTUR Bat protection active | System | WTUR | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 49
245 | 9049 | WTUR Parameterized P red. | System | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 50
246 | 9050 | WTUR Parameterized speed red. | System | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 51
248 | 9051 | WTUR Red. op. soft cut out | System | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 52
249 | 9052 | WTUR Soft cut out par. implausible | System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 53
250 | 9053 | WTUR Update active | System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Service Partner | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 54
251 | 9054 | WTUR Stop for man./aut. reboot | System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 55
252 | 9055 | WTUR Update failed | System | WTUR | Warning | No |  |  | Operation Control | See only | See only | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 56
253 | 9056 | WTUR Manual reboot | System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 57
254 | 9057 | WTUR Man. shutdown error | System | WTUR | Error | No |  |  | Operation Control | See only | See only | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 58
305 | 9058 | WTUR Brake control | System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 59
308 | 9059 | WTUR Max. braking time OP20 | System | WTUR | Error | No | *15min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 60
310 | 9060 | WTUR Max. braking time BP10 | System | WTUR | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 61
320 | 9061 | WTUR Max. braking time BP20 | System | WTUR | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 62
325 | 9062 | WTUR Max. braking time BP30 | System | WTUR | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 63
330 | 9063 | WTUR Max. braking time BP40 | System | WTUR | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 64
331 | 9064 | WTUR Parameter setting BP40 implausible | System | WTUR | Error | No |  |  | See only | See only | See only | See only | See only | Covert | See only | See only | [5 empty] | development: 'See Only' written as 'See only'; sales: 'See Only' written as 'See only'; tcc: 'See Only' written as 'See only'; service: 'See Only' written as 'See only'; turbine_operator_package: 'See Only' written as 'See only'; service_partner: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 65
332 | 9065 | WTUR Max. braking time BP70 | System | WTUR | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 66
335 | 9066 | WTUR Max. braking time BP70 | System | WTUR | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 67
340 | 9067 | WTUR Max. braking time BP70 | System | WTUR | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 68
360 | 9068 | WTUR Timeout systemtest 1 | System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 69
365 | 9069 | WTUR Timeout systemtest 2 | System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 70
370 | 9070 | WTUR Timeout systemtest 3 | System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 71
400 | 9071 | WTUR Manual operation | System | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 72
402 | 9072 | WTUR Semi-automatic operation | System | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 73
405 | 9073 | WTUR Stop manual operation | System | WTUR | Info | No |  |  | Department | See only | See only | See only | Preventive Maintenance | Covert | See only | See only | [5 empty] | sales: 'See Only' written as 'See only'; tcc: 'See Only' written as 'See only'; service: 'See Only' written as 'See only'; service_partner: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 74
412 | 9074 | WTUR Test brake program 70 | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 75
414 | 9075 | WTUR Test brake program 70 | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 76
415 | 9076 | WTUR Test brake program 70 | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 77
416 | 9077 | WTUR Test brake program 40 | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 78
418 | 9078 | WTUR Test brake program 30 | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 79
420 | 9079 | WTUR Test brake program 20 | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 80
422 | 9080 | WTUR Test brake program 10 | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 81
424 | 9081 | WTUR Test operational program 20 | System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 82
430 | 9082 | WTUR No-load rotation active | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 83
435 | 9083 | WTUR No speed development | System | WTUR | Error | Yes | *10s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 84
440 | 9084 | WTUR Repeating error OP 0 | System | WTUR | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 85
455 | 9085 | WTUR Repeating error BP20 | System | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 86
460 | 9086 | WTUR Repeating error BP30 | System | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 87
465 | 9087 | WTUR Repeating error BP40 | System | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 88
468 | 9088 | WTUR Repeating error BP70 | System | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 89
470 | 9089 | WTUR Repeating error BP70 | System | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 90
475 | 9090 | WTUR Repeating error BP70 | System | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 91
4620 | 9091 | WTUR Tower base temp. impermissible | System | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 92
586 | 9200 | WTUR Dev. single pitch angle targ. | Control System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 93
589 | 9201 | WTUR Targ. pitch angle coll. dev. | Control System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 94
693 | 9202 | WTUR Coll. pitch targ.rate exceed. | Control System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; turbine_operator_package: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 95
694 | 9203 | WTUR Sel. pitch targ.rate exceed. | Control System | WTUR | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; turbine_operator_package: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 96
7001 | 9204 | WTUR Task runtime failure 1ms | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 97
7002 | 9205 | WTUR Task runtime failure 5ms | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 98
7003 | 9206 | WTUR Task runtime failure 10 ms | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 99
7004 | 9207 | WTUR Task runtime failure grid measuring | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 100
7005 | 9208 | WTUR Division by zero | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 101
7008 | 9209 | WTUR Reboot necessary after update | Control System | WTUR | Info | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 102
7009 | 9210 | WTUR Unexpected reboot | Control System | WTUR | Warning | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 103
7010 | 9211 | WTUR Parameter unreadable | Control System | WTUR | Error | No |  |  | Operation Control | See only | See only | See only | Preventive Maintenance | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 104
7011 | 9212 | WTUR Loading parameters | Control System | WTUR | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 105
7012 | 9213 | WTUR Manual snapshot | Control System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 106
7013 | 9214 | WTUR Alarm call test | Control System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 107
7014 | 9215 | WTUR Cond. snapshot | Control System | WTUR | Info | No |  |  | SCADA User | Covert | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 108
7016 | 9216 | WTUR Parameter outside limits | Control System | WTUR | Warning | No |  |  | Operation Control | See only | See only | See only | Preventive Maintenance | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 109
7017 | 9217 | WTUR Parameter outside limits stop | Control System | WTUR | Error | No |  |  | Operation Control | See only | See only | See only | Preventive Maintenance | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 110
7018 | 9218 | WTUR Parameter update active | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | See only | Preventive Maintenance | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 111
7019 | 9219 | WTUR Unsafe parametrization | Control System | WTUR | Error | No |  |  | Operation Control | See only | See only | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 112
7025 | 9220 | WTUR Configuration error | Control System | WTUR | Error | No |  |  | Operation Control | See only | See only | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 113
7026 | 9221 | WTUR License error | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 114
7027 | 9222 | WTUR Runtime error | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 115
7028 | 9223 | WTUR Software exception error | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 116
7029 | 9224 | WTUR File transfer error | Control System | WTUR | Info | No | *2d |  | Operation Control | See only | See only | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 117
7030 | 9225 | WTUR Controller flags implausible | Control System | WTUR | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 118
7031 | 9226 | WTUR Controller parameter setting implausible | Control System | WTUR | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 119
7035 | 9227 | WTUR Controller feed forward function reduced 50% | Control System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 120
7036 | 9228 | WTUR Controller feed forward function deactivated | Control System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 121
7040 | 9229 | WTUR Set point above rated speed | Control System | WTUR | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 122
7050 | 9230 | WTUR PT100 top box defect | Control System | WTUR | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 123
7052 | 9231 | WTUR P red. incr. top box temp. | Control System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 124
7053 | 9232 | WTUR Top box temperature high | Control System | WTUR | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 125
7054 | 9233 | WTUR Top box temperature low | Control System | WTUR | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 126
7055 | 9234 | WTUR Error meas. top box temp. | Control System | WTUR | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 127
7057 | 9235 | WTUR Heating/fan top box faulty | Control System | WTUR | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 128
7058 | 9236 | WTUR Fuses overload | Control System | WTUR | Warning | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Standard | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 129
7059 | 9237 | WTUR Max. top box temp | Control System | WTUR | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 130
7085 | 9238 | WTUR Comm. error switch top box | Control System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 131
7090 | 9239 | WTUR Comm. error base box switch | Control System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 132
7092 | 9240 | WTUR IEC interface read requests | Control System | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Commissioning | See only | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 133
7160 | 9241 | WTUR Manual stop on site - maint. required | Control System | WTUR | Error | No |  |  | Operation Control | Covert | See only | Commissioning | See only | Covert | See only | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 134
7190 | 9242 | WTUR 10ms task runtime high | Control System | WTUR | Info | Yes | *0 ms |  | Operation Control | Covert | Telenotdienst | Commissioning | Covert | Covert | Covert | Covert | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 135
7250 | 9243 | WTUR HC/WTC comm. version conflict | Control System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 136
7324 | 9244 | WTUR Check time synchronization | Control System | WTUR | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Premium | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 137
7325 | 9245 | WTUR Time sync. failed (SNTP error) | Control System | WTUR | Warning | No | *0 ms |  | Department | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | See only | Premium | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 138
7335 | 9246 | WTUR mconfig.ini check failed | Control System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 139
7340 | 9247 | WTUR TwC algorithm implausible | Control System | WTUR | Warning | No |  | *1h | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 140
7350 | 9248 | WTUR New initialization rotor pos. | Control System | WTUR | Info | No |  | *8min | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 141
7400 | 9249 | WTUR High CPU temperature | Control System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 142
7401 | 9250 | WTUR Max. temperature CPU | Control System | WTUR | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 143
7402 | 9251 | WTUR CPU Failure RTC | Control System | WTUR | Warning | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 144
7403 | 9252 | WTUR CPU NVRAM battery | Control System | WTUR | Warning | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 145
7404 | 9253 | WTUR CPU memory error | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 146
7415 | 9254 | WTUR PLC hardware error | Control System | WTUR | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 147
7421 | 9255 | WTUR CAN bus module firmware | Control System | WTUR | Error | No | *5s | *5s | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 148
7425 | 9256 | WTUR Profinet communication (nacelle cool.sys.) disrupted | Control System | WTUR | Warning | No | *5s | *5s | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 149
7610 | 9257 | WTUR Firmware update required | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 150
7611 | 9258 | WTUR Firmware update failed | Control System | WTUR | Warning | No |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 151
151 | 9300 | WTUR SLC app. not running | Safety | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 152
152 | 9301 | WTUR SLC app. not in SAFE mode | Safety | WTUR | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 153
153 | 9302 | WTUR SLC SF max. cable winding | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 154
154 | 9303 | WTUR SLC SF generator temperature | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 155
155 | 9304 | WTUR SLC SF system monitoring | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 156
156 | 9305 | WTUR SLC SF overspeed | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 157
157 | 9306 | WTUR SLC SF max. tower oscillation | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 158
158 | 9307 | WTUR SLC SF max. rotor brake pad temp. | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 159
159 | 9308 | WTUR SLC SF emergency stop | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 160
170 | 9309 | WTUR SLC MF brake request HC | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 161
171 | 9310 | WTUR SLC MF converter grid disconnection | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 162
172 | 9311 | WTUR SLC MF torque protection | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 163
173 | 9312 | WTUR SLC MF max. tower oscillation analog | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 164
175 | 9313 | WTUR SLC error | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 165
176 | 9314 | WTUR SLC warning | Safety | WTUR | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 166
177 | 9315 | WTUR SLC MF blade regulation control | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 167
178 | 9316 | WTUR SLC MF safe operation speed limit | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 168
181 | 9317 | WTUR SLC implaus. speed | Safety | WTUR | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 169
182 | 9318 | WTUR SLC interface error | Safety | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 170
183 | 9319 | WTUR SLC run-time limit active | Safety | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 171
9000 | 9900 | WTUR P output externally reduced | External | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 190
9001 | 9901 | WTUR P limit. extern. IEC | External | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 191
9006 | 9902 | WTUR dU limit. extern. IEC | External | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 192
9022 | 9903 | WTUR Stop ext. prot.dev. | External | WTUR | Info | No | *10s |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 193
9085 | 9904 | WTUR Fallback P limit. failure IEC | External | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 194
9086 | 9905 | WTUR IEC failure: stop | External | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 195
9087 | 9906 | WTUR Fallback dU limit. failure IEC | External | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 196
9210 | 9907 | WTUR Externally stopped | External | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 197
9211 | 9908 | WTUR External stop IEC | External | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 198
8000 | 9930 | WTUR Park master stop | Farm | WTUR | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 199
8001 | 9931 | WTUR Slave tripping | Farm | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 200
8002 | 9932 | WTUR Emer. power op. active | Farm | WTUR | Info | No | *100ms |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 201
8100 | 9933 | WTUR Comm. failure FDM all clients | Farm | WTUR | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 202
8105 | 9934 | WTUR Parkmaster operation failed | Farm | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Advanced | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 203
8200 | 9935 | WTUR PMU snapshot | Farm | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 204
8300 | 9936 | WTUR Icing (farm) | Farm | WTUR | Info | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 205
8400 | 9937 | WTUR Comm. failure FPM | Farm | WTUR | Warning | No | *2min |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 206
8401 | 9938 | WTUR Comm. failure FPM: stop | Farm | WTUR | Error | No | *10s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 207
8402 | 9939 | WTUR No assignment to a PMU | Farm | WTUR | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 208
8405 | 9940 | WTUR Fallback setpoints active | Farm | WTUR | Info | No | *10s |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 209
8410 | 9941 | WTUR IP duplicate in WF network | Farm | WTUR | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 210
8420 | 9942 | WTUR BCP master with same seg.no. | Farm | WTUR | Warning | No |  |  | Department | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 211
691 | 9960 | WTUR Targ. pitch angle implaus. | Feedback Control | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; turbine_operator_package: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 212
696 | 9961 | WTUR Indiv. setp.pitch ang. offset incorr. | Feedback Control | WTUR | Error | Yes |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | [5 empty] | sales: 'See Only' written as 'See only'; turbine_operator_package: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 213
9090 | 9970 | 7300 | Interface | WTUR | Warning | No | *0 ms | *0 ms | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | Professional | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 214
403 | 9980 | WTUR PMU active power semi-aut. op. | Power Management | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 215
404 | 9981 | WTUR PMU react. power semi-aut. op. | Power Management | WTUR | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | [5 empty] | sales: 'See Only' written as 'See only'; customer: 'See Only' written as 'See only' | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 216
3400 | 9990 | WTUR UPS warning | UPS | WTUR | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 217
3410 | 9991 | WTUR UPS error | UPS | WTUR | Error | No | *10min |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 218
3420 | 9992 | WTUR UPS buffer time too short | UPS | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 219
3430 | 9993 | WTUR UPS error | UPS | WTUR | Warning | No |  |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 220
3440 | 9994 | WTUR UPS air conditioning faulty | UPS | WTUR | Warning | No | *10s |  | SCADA User | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | [6 empty] | PROPOSED | Statuscode 4XM Rise0B.xlsx, sheet WTUR, row 221

## HC
legacy_number | new_number | description | functional_group | logical_node | type | up_down_counter | parameter_set_delay | parameter_reset_delay | development | sales | tcc | service | turbine_operator_package | grid_operator | service_partner | customer | cause | directive | planning_priority | planning_estimation | planning_comment | note | status | source
10500 | 11001 | Incorrect monit.function parameter | Control System | WTUR | Error | No |  |  | Department | See only | See only | Service and Maintenance | See only | Covert | See only | See only | A monitoring function is incorrectly parametrized. This may affect the following monitoring functions: - overspeed setpoint angle monitor | Initiate a service call. Load the correct parameter file. | 3 |  | Test on Proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 2
10550 | 11002 | Pitch back reboot HC | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The hub controller has performed a reboot, pitch back is triggered. | If the reboot was expected, no reaction is necessary. Otherwise inform TCC Level 2, secure the log files with the M-Manager and forward them to Technical Support (OMTE operation control). | 3 |  | Test on Proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 3
7001 | 11003 | Task runtime failure 1ms | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Service Partner | See only | Major control system fault: the 1 ms task took too long. | Inform TCC Level 2. If the status occurred during the booting of the control system (e.g., after grid restoration or during commissioning), it can be reset once. Otherwise initiate a service call. Secure the log files with the M-Manager and forward them to Technical Support (OMTE operation control). Observe SI/SA 001 for a reset! | 3 |  | Test on Proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 4
7002 | 11004 | Task runtime failure 5ms | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Service Partner | See only | Major control system fault: the 5 ms task took too long. | Inform TCC Level 2. If the status occurred during the booting of the control system (e.g., after grid restoration or during commissioning), it can be reset once. Otherwise initiate a service call. Secure the log files with the M-Manager and forward them to Technical Support (OMTE operation control). Observe SI/SA 001 for a reset! | 3 |  | Test on Proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 5
7003 | 11005 | Task runtime failure 10 ms | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Service Partner | See only | Major control system fault: the 10 ms task took longer than 10 ms. | Inform TCC Level 2. If the status occurred during the booting of the control system (e.g., after grid restoration or during commissioning), it can be reset once. Otherwise initiate a service call. Secure the log files with the M-Manager and forward them to Technical Support (OMTE operation control). Observe SI/SA 001 for a reset! | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 6
7005 | 11006 | Division by zero | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Troubleshooting | Covert | Service Partner | See only | Major control system fault: a division by zero occurred during an internal calculation in the control system. | Inform TCC Level 2. If the status occurred during the booting of the control system (e.g., after grid restoration or during commissioning), it can be reset once. Otherwise initiate a service call. Secure the log files with the M-Manager and forward them to Technical Support (OMTE operation control). Observe SI/SA 001 for a reset! | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 7
7008 | 11007 | Reboot necessary after update | Control System | WTUR | Info | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The operator has initiated a software update and files that will only become effective after a reboot of the control system have been exchanged. | Use the access list to clarify who caused the status and why it was caused. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 8
7009 | 11008 | Unexpected reboot | Control System | WTUR | Warning | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Ext. Service Provider | See only | The control system has performed an unexpected reboot. | No action is necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 9
7010 | 11009 | Parameter unreadable | Control System | WTUR | Error | No |  |  | Operation Control | See only | See only | See only | Preventive Maintenance | Covert | See only | See only | An unexpected event prevented the parameter file from being read correctly. | Reload the parameter file. The WTG may restart after resetting the status code. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 10
7011 | 11010 | Loading parameters | Control System | WTUR | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | An operator initiates loading the parameters in SCADA Access Monitoring. The hub controller must be in the vane position or manual operation operating mode for this. | Use the access list to check who activated the status and why it was activated. This status cannot be reset manually. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 11
7012 | 11011 | Manual snapshot | Control System | WTUR | Info | No |  |  | SCADA User | Sales | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | A manual snapshot was triggered in the "Service" menu in SCADA Access Monitoring. | No reaction required. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 12
7014 | 11012 | Cond. snapshot | Control System | WTUR | Info | No |  |  | SCADA User | Covert | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | A so-called "conditional snapshot" is defined in SCADA Access Monitoring and the criteria for triggering the snapshot are met. The status code and the snapshot triggered by it are only used for data acquisition. | No reaction required. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 13
7016 | 11013 | Parameter outside limits | Control System | WTUR | Warning | No |  |  | Operation Control | See only | See only | See only | Preventive Maintenance | Covert | See only | See only | One parameter is not between the minimum and maximum limit values. The parameter was modified manually or due to a fault in the control system. | No action required because a user who has typically exceeded the limit values on purpose has logged on. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 14
7017 | 11014 | Parameter outside limits stop | Control System | WTUR | Error | No |  |  | Operation Control | See only | See only | See only | Preventive Maintenance | Covert | See only | See only | One parameter is not between the minimum and maximum limit values and no user is logged on locally or a user has been logged on locally for over 8 hours. The parameter was modified manually or due to a fault in the control system. | Check which parameters were modified by which user. Contact the user to find out the reasons. If the user is unknown, find out if the parameters were modified without authorization or due to a technical error. Following consultation if applicable, load the original parameter set and restart the WTG. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 15
7018 | 11015 | Parameter update active | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | See only | Preventive Maintenance | Covert | See only | See only | A parameter update is currently being performed on the WTG. | No action is necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 16
7025 | 11016 | Configuration error | Control System | WTUR | Error | No |  |  | Operation Control | See only | See only | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | The INTFHDL task collects information on the status of the configuration and the execution of various software modules. If a software module reports an error, the status of the configuration in INTFHDL is set to -1. The control task evaluates this information. More detailed information on the module error can be found in the "logfile.txt" log file. | The WTG cannot be started up in this state. Save the "logfile.txt" file from the /nvram0 directory and contact SCADA development. | 3 |  | Test on Proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 17
7026 | 11017 | License error | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | A license is invalid, corrupt, or missing. More detailed information on the license error can be found in the "logfile.txt" log file | Save the "logfile.txt" file from the /nvram0 directory and contact SCADA Development. | 3 |  | Repeat Timer will decrease: test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 18
7027 | 11018 | Runtime error | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | The INTFHDL task collects information on the status of various software modules' runtimes. If a software module signals a runtime error, the status of the runtime in INTFHDL is set to -1. The control task evaluates this information. More detailed information on the module error can be found in the "logfile.txt" log file. | Save the "logfile.txt" file from the /nvram0 directory and contact SCADA Development. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 19
7028 | 11019 | Software exception error | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | The BUGHUNT task collects information on fatal exception errors in the runtime of various software modules. If a software module triggers a fatal exception error, the status of the fatal exception error in BUGHUNT is set to -1. The control task evaluates this information. More detailed information on the module error can be found in the "logfile.txt" log file. | Save the "logfile.txt" file from the /nvram0 directory and contact SCADA Development. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 20
7029 | 11020 | File transfer error | Control System | WTUR | Info | No | *2d |  | Operation Control | See only | See only | Commissioning | Troubleshooting Advanced | Covert | Service Partner | See only | The REPOST task transmits data from the control system to various recipients. An error occurred in the process. | Check the transfer list in SAM. If a problem with file transfer for server 2-10 persists, check the parameters and, as necessary, notify SCADA support. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 21
7190 | 11021 | 10ms task runtime high | Control System | WTUR | Info | Yes | *0 ms |  | Operation Control | Covert | Telenotdienst | Commissioning | Covert | Covert | Covert | Covert | The 10 minute average runtime of the 10ms tasks is higher than the value of parameter "10ms task runtime". | No reaction required. | 3 |  | Repeat Timer will decrease: test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 22
7191 | 11022 | Error variable initiation | Control System | WTUR | Error | No |  |  | Operation Control | Covert | Telenotdienst | Commissioning | Covert | Covert | Covert | Covert | The initialization procedure for a critical variable was carried out for too long/too frequently. This may affect the following functions: - speed setpoint monitoring - overspeed setpoint angle monitor | Shut down the WTG, inform SCADA development department. | 3 |  | Repeat Timer will decrease: test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 23
7250 | 11023 | HC/WTC comm. version conflict | Control System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | There is a version conflict regarding Bluecom communication between the hub controller (HC) and the wind turbine control system (WTC). | Ensure that software versions are installed on the hub controller and the wind turbine control system that are compatible with Bluecom communication. Other software versions must accordingly be installed on the hub controller and/or the wind turbine control system. Note on diagnostics: the Bluecom communication version number is available in both the log file of the hub controller and the log file of the wind turbine control system. | 3 |  | Repeat Timer will decrease: test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 24
7324 | 11024 | Check time synchronization | Control System | WTUR | Warning | No |  |  | SCADA User | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | Premium | A big time leap occurred during the last time synchronization. Big leaps during the time synchronization may cause data loss. One-off occurrence of this status code is not unusual during installation and commissioning of the wind farm. Each wind farm includes a wind turbine or Power Management Unit which has the function of a central time server (parameter "SNTP master" activated in "Farm" functional group, recognizable by the clock symbol in the wind farm overview, typically wind turbine no. 1). This wind turbine is synchronized with the central time server at Easynet. All other wind farm units synchronize their system time with the server using the Simple Network Time Protocol (SNTP). This status code only serves as a warning. | 1. Check the time of the time server in the wind farm. 2. Check the time synchronization in the wind farm. 3. Check the data volume of the control systems for completeness after importing the data into Senvion SCADA Solutions. Perform the following steps if the control system does not transmit any log files and only an attempt to establish a connection is displayed in the "Reports/Transfer" menu: 1. Stop the wind turbine in SCADA Access Monitoring. 2. Delete the /cfc0/REJAVLIB/rejavlib.rtn retain file with the M-Manager. 3. Quickly reboot the control system with the M-Manager. 4. Manually trigger file transmission in SCADA Access Monitoring (activate the "Test file transmission" parameter in the "Service/Mainten." menu). | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 25
7325 | 11025 | Time sync. failed (SNTP error) | Control System | WTUR | Warning | No | *0 ms |  | Department | Sales | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | See only | Premium | Cyclical synchronization with the SNTP server (simple network time protocol) has failed several times over a longer period. Occurrence of this status code is not unusual during installation and commissioning of the wind farm. Each wind farm includes a wind turbine or Power Management Unit which has the function of a central time server (parameter "SNTP master" activated in "Farm" functional group, recognizable by the clock symbol in the wind farm overview, typically wind turbine no. 1). This wind turbine is synchronized with the central time server at Easynet. All other wind farm units synchronize their system time with the server. | If the status code is permanently active: check the IP addresses of the SNTP time server and the data connection. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 26
7335 | 11026 | mconfig.ini check failed | Control System | WTUR | Error | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | Check of the cfc0/mconfig.ini file failed. Unauthorized modifications to the file were made. The file may only be modified as described in the respective work instructions for commissioning and software updates. This status cannot be reset manually. | Copy the original "mconfig.ini" file from the release directory into the "cfc0/" main directory of the CompactFlash card in the control system with the M-Manager. Then reboot the control system. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 27
7400 | 11027 | High CPU temperature | Control System | WTUR | Warning | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The temperature of the CPU (i.e. the processor module of the control system) is close to the warranty temperature guaranteed by the manufacturer. ATTENTION: The temperature value ("CPU temperature high" = 95 %) provides a percentage of the maximum permissible temperature, i.e., a relative value and not a degree value. This status code only serves as a warning. | Check hub and main box temperature. If no overtemperatures in the main box have occurred on this WTG before and the status code was caused by unusually high hub temperatures: No reaction required (provided that no other status codes are active). Otherwise initiate a service call and have the processor module checked. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 28
7401 | 11028 | Max. temperature CPU | Control System | WTUR | Error | No | *1s |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The temperature of the CPU (i.e. the processor module of the control system) is outside the warranty temperature guaranteed by the manufacturer. This may reduce the lifespan of the CPU. ATTENTION: The temperature value ("CPU stop Temp." = 105 %) provides a percentage of the maximum permissible temperature, i.e., a relative value and not a degree value. | Initiate a service call and have the processor module checked. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 29
7402 | 11029 | CPU Failure RTC | Control System | WTUR | Warning | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The CPU (processor module of the control system) signals an error during the check of the real-time clock. This status code only serves as a warning. | Stop the wind turbine and reboot the hub controller using the M-Manager. If this does not remedy the fault, initiate a service call and replace the processor module of the control system. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 30
7403 | 11030 | CPU NVRAM battery | Control System | WTUR | Warning | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The CPU (processor module of the control system) signals that the NVRAM battery is almost empty during the check by the program. This status code only serves as a warning. | Initiate a service call or inform the foreman that the processor module of the control system needs to be replaced. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 31
7404 | 11031 | CPU memory error | Control System | WTUR | Error | No |  |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | Major control system fault: the CPU (processor module of the control system) signals an error in the memory range during the check by the program. | Inform TCC Level 2. If the status occurred during the booting of the control system (e.g., after grid restoration or during commissioning), it can be reset once. Otherwise initiate a service call. Secure the log files with the M-Manager and forward them to Technical Support (OMTE operation control). Observe SI/SA 001 for a reset. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 32
7415 | 11032 | PLC hardware error | Control System | WTUR | Error | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | A PLC hardware module signals a fault. A faulty PLC module normally causes a lot of subsequent errors. | If the status is permanently active or occurs repeatedly (status code 10050), check which module is faulty in the "Monitoring" menu ("Control system" functional group, "Module monitoring" category). Initiate a service call and replace the faulty module. If the fault still occurs after the faulty module has been replaced, check the DIP switch settings of the module. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 33
7420 | 11033 | CAN bus error | Control System | WTUR | Error | No | *5s | *5s | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | CAN bus monitoring has detected an error. A communication error at the CAN bus may cause many subsequent errors. | If the status is permanently active or occurs repeatedly (status code 10050), initiate a service call. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 34
7421 | 11034 | CAN bus module firmware | Control System | WTUR | Error | No | *5s | *5s | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | Monitoring of the CAN bus module CM202 firmware has detected legacy firmware. Firmware V4.x and above must be used with an MC CPU. | Check the module firmware. Update the firmware if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 35
7610 | 11035 | Firmware update required | Control System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Service Partner | See only | The firmware of at least one control module is obsolete. | A firmware update is required. | 1 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 36
7611 | 11036 | Firmware update failed | Control System | WTUR | Warning | No |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Service Partner | See only | The firmware update for at least one control module has failed. | Save the "logfile.txt" and "logfile.old" files from the /nvram0 directory, save the /cfc0/ directory, and contact SCADA development. | 1 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 37
11500 | 11101 | Pitch back comm. WTG | Field Bus | WTUR | Error | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The communication between the hub controller and the control of the WTG is defective. The hub controller has not received correct or complete data from the WTG control system within the time set in the parameter "Time comm.failure WTG". Possible causes: - Slip ring defective or no continuity in fiber-optic cable path. - Problem with connectors or connections of the fiber optic cable between the hub controller and the controller of the WTG. - Problem with connectors or connections between the communication switch in the rotor hub and the hub controller. - Problem with connectors or connections between the communication switch of the WTG and the control system of the WTG. - The communication switches (rotor hub & control system of the WTG) are not correctly configured or their connections are not connected. - The voltage supply of the communication switches (rotor hub & control system of the WTG) is defective. - Incorrect hub box version parameterized on the WTG control system - In the mpc_cfg.txt of the hub controller, the correct Bluecom segment number is not entered. - The software versions on the hub controller and on the controller of the WTG are not compatible with respect to communication. - Stopping of a control task of the hub controller or the controller of the WTG (for example, program runtime error). | Check the frequency of pitch communication errors with the corresponding operating hours meter. If no communication problems have occurred on this wind turbine before, it may be started once. Otherwise initiate a service call. | 1 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 38
11811 | 11102 | Comm. failure B encoder 1 | Field Bus | WTUR | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The hub controller has not received a new data packet from B encoder 1 for multiple receive cycles. Communication is interrupted or the encoder is defective. | Initiate a service call. | 2 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 39
11812 | 11103 | Comm. failure B encoder 2 | Field Bus | WTUR | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The hub controller has not received a new data packet from B encoder 2 for multiple receive cycles. Communication is interrupted or the encoder is defective. | Initiate a service call. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 40
11813 | 11104 | Comm. failure B encoder 3 | Field Bus | WTUR | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The hub controller has not received a new data packet from B encoder 3 for multiple receive cycles. Communication is interrupted or the encoder is defective. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 41
11851 | 11105 | Comm. failure pitch conv. 1 | Field Bus | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The hub controller has not received a new data packet from pitch converter 1 for multiple receive cycles. Communication is interrupted or the pitch converter is defective. | Initiate a service call. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 42
11852 | 11106 | Comm. failure pitch conv. 2 | Field Bus | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The hub controller has not received a new data packet from pitch converter 2 for multiple receive cycles. Communication is interrupted or the pitch converter is defective. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 43
11853 | 11107 | Comm. failure pitch conv. 3 | Field Bus | WTUR | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The hub controller has not received a new data packet from pitch converter 3 for multiple receive cycles. Communication is interrupted or the pitch converter is defective. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 44
11860 | 11108 | Failure comm. blade load sensors | Field Bus | WTUR | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The hub controller has not received a new data packet from the blade load sensors for multiple receive cycles. Communication is interrupted or the sensors are defective. Possible causes: - Problem with connectors, cabling or shielding between control system hub controller and blade load sensors - Defect of blade load sensors or the CANopen interface on the MPC processor module | Inform the SCADA development department. Initiate service call if necessary. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 45
0 | 11151 | System OK | System | WTUR | Info | No |  |  | See only | See only | See only | See only | Covert | Covert | See only | See only | The pitch is error-free. There is no fault, warning or information pending. This status code is activated if no other status has been set. Otherwise the status will be reset. | No reaction required. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 46
250 | 11152 | Update active | System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Service Partner | See only | The update function was initiated in the ''Service'' menu in SCADA Access Monitoring. | This status code is active while an update is being performed. It will be automatically reset if the update fails (status code 252) or is completed successfully. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 47
251 | 11153 | Stop for man./aut. reboot | System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | The reboot function was triggered in the "Service" menu in SCADA Access Monitoring using the "Reboot controller" button. | Wait until the control system has been successfully booted | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 48
252 | 11154 | Update failed | System | WTUR | Warning | No |  |  | Operation Control | See only | See only | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | The update failed. Possible causes: - The installation file is missing or faulty - an error or timeout occurred during process data backup, parameter backup, file transmission or backup of the average value selection | Repeat the update. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 49
253 | 11155 | Manual reboot | System | WTUR | Info | No |  |  | Operation Control | See only | See only | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | All three rotor blades were moved to the limit switches by pressing the "Reboot controller" button in the "Service" menu and the control system will reboot shortly. | Wait until the control system has been successfully booted. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 50
254 | 11156 | Man. shutdown error | System | WTUR | Error | No |  |  | Operation Control | See only | See only | Commissioning | Preventive Maintenance | Covert | Service Partner | See only | An error occurred while shutting down the WTG. | Check the process data backup files. If necessary, reboot the control system manually for an update to become effective. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 51
402 | 11157 | Semi-automatic operation | System | WTUR | Info | No |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Advanced | See only | Semi-automatic operation has been activated. Semi-automatic operation is activated in the "Service" menu. | If the user has not identified himself by registering with PMS: Clarify who is at the WTG (call operator or Service) and why semi-automatic operation has been activated. Deactivate semi-automatic operation if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 52
13511 | 12001 | Sim.ang. D enc. <> act.ang. A enc. 1 | Blades | WROT | Error | Yes | *400ms |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Covert | Covert | Ext. Service Provider | See only | On the basis of the pitch angle setpoint, the pitch estimator in the HC calculates expected actual values that are then compared with the measured actual pitch angles for each rotor blade and encoder. The simulated value for the pitch angle on axis 1 calculated by the pitch estimator deviates from the measured actual angle of the A encoder by more than is permitted by active triggering threshold. The active triggering threshold depends on the current pitch angle setpoint - a distinction of accuracy is made between angles smaller and greater than the value set in parameter "Est. changeover angle". The acceptable deviations are set in parameters "Est. big trig.thresh." and "Est. small trig.thresh. A". Possible causes: - Poor communication between the hub controller and control system - Encoder defect - Pitch converter error - Mechanical problems - Hub controller malfunction - Incorrect parametrization | Evaluate the snapshot to identify the cause of the error. Inform TCC Level 2. 1. Evaluate the status list and the event list: in which operation mode did the error occur (e.g., start-up procedure, shut-down procedure, normal operation, no pitch activity)? 2. Check pitch angles (both encoder systems) and, if necessary, other relevant factors, such as pitch motor currents, WTG speed, wind conditions, etc. in the snapshot. 3. Check actual values of the pitch angles (both encoder systems) in the "Monitoring" menu and move rotor blades manually for testing if necessary. If necessary, initiate a service call. If no deviations are detected, start the WTG and monitor the start-up procedure. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 53
13512 | 12002 | Sim.ang. D enc. <> act.ang. A enc. 2 | Blades | WROT | Error | Yes | *400ms |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Covert | Covert | Ext. Service Provider | See only | On the basis of the pitch angle setpoint, the pitch estimator in the HC calculates expected actual values that are then compared with the measured actual pitch angles for each rotor blade and encoder. The simulated value for the pitch angle on axis 2 calculated by the pitch estimator deviates from the measured actual angle of the A encoder by more than is permitted by active triggering threshold. The active triggering threshold depends on the current pitch angle setpoint - a distinction of accuracy is made between angles smaller and greater than the value set in parameter "Est. changeover angle". The acceptable deviations are set in parameters "Est. big trig.thresh." and "Est. small trig.thresh. A". Possible causes: - Poor communication between the hub controller and control system - Encoder defect - Pitch converter error - Mechanical problems - Hub controller malfunction - Incorrect parametrization | Evaluate the snapshot to identify the cause of the error. Inform TCC Level 2. 1. Evaluate the status list and the event list: in which operation mode did the error occur (e.g., start-up procedure, shut-down procedure, normal operation, no pitch activity)? 2. Check pitch angles (both encoder systems) and, if necessary, other relevant factors, such as pitch motor currents, WTG speed, wind conditions, etc. in the snapshot. 3. Check actual values of the pitch angles (both encoder systems) in the "Monitoring" menu and move rotor blades manually for testing if necessary. If necessary, initiate a service call. If no deviations are detected, start the WTG and monitor the start-up procedure. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 54
13513 | 12003 | Sim.ang. D enc. <> act.ang. A enc. 3 | Blades | WROT | Error | Yes | *400ms |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Covert | Covert | Ext. Service Provider | See only | On the basis of the pitch angle setpoint, the pitch estimator in the HC calculates expected actual values that are then compared with the measured actual pitch angles for each rotor blade and encoder. The simulated value for the pitch angle on axis 3 calculated by the pitch estimator deviates from the measured actual angle of the A encoder by more than is permitted by active triggering threshold. The active triggering threshold depends on the current pitch angle setpoint - a distinction of accuracy is made between angles smaller and greater than the value set in parameter "Est. changeover angle". The acceptable deviations are set in parameters "Est. big trig.thresh." and "Est. small trig.thresh. A". Possible causes: - Poor communication between the hub controller and control system - Encoder defect - Pitch converter error - Mechanical problems - Hub controller malfunction - Incorrect parametrization | Evaluate the snapshot to identify the cause of the error. Inform TCC Level 2. 1. Evaluate the status list and the event list: in which operation mode did the error occur (e.g., start-up procedure, shut-down procedure, normal operation, no pitch activity)? 2. Check pitch angles (both encoder systems) and, if necessary, other relevant factors, such as pitch motor currents, WTG speed, wind conditions, etc. in the snapshot. 3. Check actual values of the pitch angles (both encoder systems) in the "Monitoring" menu and move rotor blades manually for testing if necessary. If necessary, initiate a service call. If no deviations are detected, start the WTG and monitor the start-up procedure. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 55
13521 | 12004 | Sim.ang. D enc. <> act.ang. B enc. 1 | Blades | WROT | Error | Yes | *400ms |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Covert | Covert | Ext. Service Provider | See only | On the basis of the pitch angle setpoint, the pitch estimator in the HC calculates expected actual values that are then compared with the measured actual pitch angles for each rotor blade and encoder. The simulated value for the pitch angle on axis 1 calculated by the pitch estimator deviates from the measured actual angle of the B encoder by more than is permitted by active triggering threshold. The active triggering threshold depends on the current pitch angle setpoint - a distinction of accuracy is made between angles smaller and greater than the value set in parameter "Est. changeover angle". The acceptable deviations are set in parameters "Est. big trig.thresh." and "Est. small trig.thresh. B". Possible causes: - Poor communication between the hub controller and control system - Encoder defect - Pitch converter error - Mechanical problems - Hub controller malfunction - Incorrect parametrization | Evaluate the snapshot to identify the cause of the error. Inform TCC Level 2. 1. Evaluate the status list and the event list: in which operation mode did the error occur (e.g., start-up procedure, shut-down procedure, normal operation, no pitch activity)? 2. Check pitch angles (both encoder systems) and, if necessary, other relevant factors, such as pitch motor currents, WTG speed, wind conditions, etc. in the snapshot. 3. Check actual values of the pitch angles (both encoder systems) in the "Monitoring" menu and move rotor blades manually for testing if necessary. If necessary, initiate a service call. If no deviations are detected, start the WTG and monitor the start-up procedure. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 56
13522 | 12005 | 13522 Sim.ang. D enc. <> act.ang. B enc. 2 | Blades | WROT | Error | Yes | *400ms |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Covert | Covert | Ext. Service Provider | See only | On the basis of the pitch angle setpoint, the pitch estimator in the HC calculates expected actual values that are then compared with the measured actual pitch angles for each rotor blade and encoder. The simulated value for the pitch angle on axis 2 calculated by the pitch estimator deviates from the measured actual angle of the B encoder by more than is permitted by active triggering threshold. The active triggering threshold depends on the current pitch angle setpoint - a distinction of accuracy is made between angles smaller and greater than the value set in parameter "Est. changeover angle". The acceptable deviations are set in parameters "Est. big trig.thresh." and "Est. small trig.thresh. B". Possible causes: - Poor communication between the hub controller and control system - Encoder defect - Pitch converter error - Mechanical problems - Hub controller malfunction - Incorrect parametrization | Evaluate the snapshot to identify the cause of the error. Inform TCC Level 2. 1. Evaluate the status list and the event list: in which operation mode did the error occur (e.g., start-up procedure, shut-down procedure, normal operation, no pitch activity)? 2. Check pitch angles (both encoder systems) and, if necessary, other relevant factors, such as pitch motor currents, WTG speed, wind conditions, etc. in the snapshot. 3. Check actual values of the pitch angles (both encoder systems) in the "Monitoring" menu and move rotor blades manually for testing if necessary. If necessary, initiate a service call. If no deviations are detected, start the WTG and monitor the start-up procedure. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 57
13523 | 12006 | Sim.ang. D enc. <> act.ang. B enc. 3 | Blades | WROT | Error | Yes | *400ms |  | Operation Control | See only | Telenotdienst | Service and Maintenance | Covert | Covert | Ext. Service Provider | See only | On the basis of the pitch angle setpoint, the pitch estimator in the HC calculates expected actual values that are then compared with the measured actual pitch angles for each rotor blade and encoder. The simulated value for the pitch angle on axis 3 calculated by the pitch estimator deviates from the measured actual angle of the B encoder by more than is permitted by active triggering threshold. The active triggering threshold depends on the current pitch angle setpoint - a distinction of accuracy is made between angles smaller and greater than the value set in parameter "Est. changeover angle". The acceptable deviations are set in parameters "Est. big trig.thresh." and "Est. small trig.thresh. B". Possible causes: - Poor communication between the hub controller and control system - Encoder defect - Pitch converter error - Mechanical problems - Hub controller malfunction - Incorrect parametrization | Evaluate the snapshot to identify the cause of the error. Inform TCC Level 2. 1. Evaluate the status list and the event list: in which operation mode did the error occur (e.g., start-up procedure, shut-down procedure, normal operation, no pitch activity)? 2. Check pitch angles (both encoder systems) and, if necessary, other relevant factors, such as pitch motor currents, WTG speed, wind conditions, etc. in the snapshot. 3. Check actual values of the pitch angles (both encoder systems) in the "Monitoring" menu and move rotor blades manually for testing if necessary. If necessary, initiate a service call. If no deviations are detected, start the WTG and monitor the start-up procedure. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 58
13550 | 12007 | B encoder set active | Blades | WROT | Info | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The B encoder system is active, the A encoder system has failed. The wind turbine can only be operated for a limited time with the B encoder system. | Check whether activation of the B encoder system is desired. The wind turbine can only be operated for 14 days using the B encoder system. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 59
13801 | 12008 | Error hardware bl.bear. lubr. pump 1 | Blades | WROT | Warning | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | The blade bearing lubrication system on axis 1 signals a warning via the digital input "No warning lubr.pump 1" (digital input IX4.23, main box, module 4, DI232, terminal 23). This can have the following causes: - Lubrication container of the pump of axis 1 is empty - Defective or missing voltage supply of lubrication pump of axis 1 | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 60
13802 | 12009 | Error hardware bl.bear. lubr. pump 2 | Blades | WROT | Warning | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | The blade bearing lubrication system on axis 2 signals a warning via the digital input "No warning lubr.pump 2" (digital input IX4.24, main box, module 4, DI232, terminal 24). This can have the following causes: - Lubrication container of the pump of axis 2 is empty - Defective or missing voltage supply of lubrication pump of axis 2 | Inform the responsible foreman. A service call must be initiated within the amount of time specified in the WTG parameter "Max.fail. blade bear.lubr.", since the WTG will otherwise be stopped automatically. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 61
13803 | 12010 | Error hardware bl.bear. lubr. pump 3 | Blades | WROT | Warning | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | The blade bearing lubrication system on axis 3 signals a warning via the digital input "No warning lubr.pump 3" (digital input IX4.25, main box, module 4, DI232, terminal 25). This can have the following causes: - Lubrication container of the pump of axis 3 is empty - Defective or missing voltage supply of lubrication pump of axis 3 | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 62
13805 | 12011 | Man. op. blade bearing lubrication | Blades | WROT | Info | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Manual operation for the blade bearing lubrication is requested on at least one axis. The status code remains active as long as the lubrication interval has not completed. | If no service call is currently taking place: use the access list to clarify who activated manual operation and why it was activated. Deactivate manual operation if necessary. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 63
13809 | 12012 | Timeout blade bear.lubr. Failure | Blades | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | On at least one axis, the blade bearing lubrication has failed for longer than the amount of time in the WTG parameter "Max.fail. blade bear.lubr.". This can have the following causes: - Lubrication containers for one or multiple pumps are empty - Defective or missing voltage supply for one or more pumps - Faulty or defective connection for one or more pumps | Initiate a service call. Following successful filling or repair of the lubrication pump(s) or other trigger reason for the status code, it may only be reset after one successful lubrication interval has been completed. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 64
13811 | 12013 | Max. runtime blade bearing lubr. pump 1 | Blades | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Activation of the rotor blade lubrication pump by the HC on axis 1 does not confirm a successfully performed lubrication interval within the expected time (WTG parameter "Max. runtime bl.bear.lubr."). This may have the following causes: - number of level changes at digital input "End cycle lubr.pump 1" (digital input IX4.26, main box, module 4, DI232, terminal 26) within WTG parameter "Blade bear.lubr. max. runtime" is less than WTG parameter "Blade bear.lubr. no. cycles" (pump is not operating sufficiently quickly, wire break at the digital input, mechanical fault in the switch) - pump is not activated via digital output "Request lubrication pump 1" (digital output QX5.13, main box, module 4, DIO232, terminal 13) (wire break at the digital output, switching parameters incorrectly set, no power supply for pump) - digital input "End cycle lubr.pump 1" (digital input IX4.26, main box, module 4, DI232, terminal 26) signals successful pressure build-up before the lubrication pump is activated. This results in continuous activation of the lubrication pump and thus to a maximum runtime. The signal "End cycle lubr.pump 1" is defective (external potential, short circuit, EMC, etc.) or the pressure in the distribution system is too high (clogged, high temperatures, etc.). - various pump hardware errors | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 65
13812 | 12014 | Max. runtime blade bearing lubr. pump 2 | Blades | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Activation of the rotor blade lubrication pump by the HC on axis 2 does not confirm a successfully performed lubrication interval within the expected time (WTG parameter "Max. runtime bl.bear.lubr."). This may have the following causes: - number of level changes at digital input "End cycle lubr.pump 2" (digital input IX4.27, main box, module 4, DI232, terminal 27) or "End cycle lubr.pump 3" (digital input IX4.28, main box, module 4, DI232, terminal 28) within WTG parameter "Blade bear.lubr. max. runtime" is less than WTG parameter "Blade bear.lubr. no. cycles" (pump is not operating sufficiently quickly, wire break at the digital input, mechanical fault in the switch) - pump is not activated via digital output "Request lubrication pump 2" (digital output QX5.14, main box, module 4, DIO232, terminal 14) (wire break at the digital output, switching parameters incorrectly set, no power supply for pump) - digital input "End cycle lubr.pump 2" (digital input IX4.27, main box, module 4, DI232, terminal 27) or "End cycle lubr.pump 3" (digital input IX4.28, main box, module 4, DI232, terminal 28) signals successful pressure build-up before the lubrication pump is activated. This results in continuous activation of the lubrication pump and thus to a maximum runtime. The signal "End cycle lubr.pump 2" or "End cycle lubr.pump 3" is defective (external potential, short circuit, EMC, etc.) or the pressure in the distribution system is too high (clogged, high temperatures, etc.). - various pump hardware errors Note: The return signal on axis 2 is dependent on the lubrication system used. If two pumps are used, the return signal "End cycle lubr.pump 3" is evaluated. | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 66
13813 | 12015 | Max. runtime blade bearing lubr. pump 3 | Blades | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Activation of the rotor blade lubrication pump by the HC on axis 3 does not confirm a successfully performed lubrication interval within the expected time (WTG parameter "Max. runtime bl.bear.lubr."). This may have the following causes: - number of level changes at digital input "End cycle lubr.pump 3" (digital input IX4.28, main box, module 4, DI232, terminal 28) within WTG parameter "Blade bear.lubr. max. runtime" is less than WTG parameter "Blade bear.lubr. no. cycles" (pump is not operating sufficiently quickly, wire break at the digital input, mechanical fault in the switch) - pump is not activated via digital output "Request lubrication pump 3" (digital output QX5.15, main box, module 4, DIO232, terminal 15) (wire break at the digital output, switching parameters incorrectly set, no power supply for pump) - digital input "End cycle lubr.pump 3" (digital input IX4.28, main box, module 4, DI232, terminal 28) signals successful pressure build-up before the lubrication pump is activated. This results in continuous activation of the lubrication pump and thus to a maximum runtime. The signal "End cycle lubr.pump 3" is defective (external potential, short circuit, EMC, etc.) or the pressure in the distribution system is too high (clogged, high temperatures, etc.). - various pump hardware errors | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 67
13821 | 12016 | Max. time press. build-up bl.bear. lubr. pump 1 | Blades | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Activation of the blade lubrication pump by the HC on axis 1 does not confirm a successful pressure build-up within the expected time (WTG parameter "Press.incr. blade bear.lubr. time"). This can have the following causes: - signal does not fall to 0 V at digital input "End cycle lubr.pump 1" (digital input IX4.26, main box, module 4, DI232, terminal 26) within WTG parameter "Press.incr. blade bear.lubr. time" (pump is not operating sufficient quickly, external potential at digital input, mechanical fault in the switch) - pump is not activated via the digital output "Request lubrication pump 1" (digital output QX5.13, main box, module 5, DIO232, terminal 13) (wire break at the digital output, switching parameters incorrectly set, no power supply for pump) - various pump hardware errors | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 68
13822 | 12017 | Max. time press. build-up bl.bear. lubr. pump 2 | Blades | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Activation of the blade lubrication pump by the HC on axis 2 does not confirm a successful pressure build-up within the expected time (WTG parameter "Press.incr. blade bear.lubr. time"). This can have the following causes: - single blade lubrication (3 pumps): signal at digital input "End cycle lubr.pump 2" (digital input IX4.27, main box, module 4, DI232, terminal 27) does not fall to 0 V within WTG parameter "Press.incr. blade bear.lubr. time" (pump is not operating sufficiently quickly, external potential at digital input, mechanical fault in the switch) - rotor blade lubrication system (1 or 2 pumps): signal at digital input "End cycle lubr.pump 3" (digital input IX4.28, main box, module 4, DI232, terminal 28) does not fall to 0 V within WTG parameter "Press.incr. blade bear.lubr. time" (pump is not operating sufficiently quickly, external potential at digital input, mechanical fault in the switch) - pump is not activated via digital output "Request lubrication pump 2" (digital output QX5.14, main box, module 5, DIO232, terminal 14) (wire break at the digital output, switching parameters incorrectly set, no power supply for pump) - various pump hardware errors | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 69
13823 | 12018 | Max. time press. build-up bl.bear. lubr. pump 3 | Blades | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Activation of the blade lubrication pump by the HC on axis 3 does not confirm a successful pressure build-up within the expected time (WTG parameter "Press.incr. blade bear.lubr. time"). This can have the following causes: - signal does not fall to 0 V at digital input "End cycle lubr.pump 3" (digital input IX4.28, main box, module 4, DI232, terminal 28) within WTG parameter "Press.incr. blade bear.lubr. time" (pump is not operating sufficient quickly, external potential at digital input, mechanical fault in the switch) - pump is not activated via the digital output "Request lubrication pump 3" (digital output QX5.15, main box, module 5, DIO232, terminal 15) (wire break at the digital output, switching parameters incorrectly set, no power supply for pump) - various pump hardware errors | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 70
13831 | 12019 | Max. time press. red. bl.bear. lubr. pump 1 | Blades | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Activation of the blade lubrication pump by the HC on axis 1 does not confirm a successful pressure reduction within the expected time (WTG parameter "Press.decr. blade bear.lubr. time") and thus a successful lubrication interval. This can have the following causes: - signal at digital input "End cycle lubr.pump 1" (digital input IX4.26, main box, module 4, DI232, terminal 26) does not rise to 24 V within WTG parameter "Press.decr. blade bear.lubr. time" (wire break at the digital input, feeder blocked, mechanical fault in the switch) - pump is not permanently activated via the digital output "Request lubrication pump 1" (digital output QX5.13, main box, module 4, DIO232, terminal 13) (external potential at digital output, switching parameters incorrectly set, no power supply for pump) - various pump hardware errors | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 71
13832 | 12020 | Max. time press. red. bl.bear. lubr. pump 2 | Blades | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Activation of the blade lubrication pump by the HC on axis 2 does not confirm a successful pressure reduction within the expected time (WTG parameter "Press.decr. blade bear.lubr. time") and thus a successful lubrication interval. This can have the following causes: - single blade lubrication (3 pumps): signal at digital input "End cycle lubr.pump 2" (digital input IX4.27, main box, module 4, DI232, terminal 27) does not rise to 24 V within WTG parameter "Press.decr. blade bear.lubr. time" (wire break at the digital input, feeder blocked, mechanical fault in the switch) - rotor blade lubrication system (1 or 2 pumps): signal at digital input "End cycle lubr.pump 3" (digital input IX4.28, main box, module 4, DI232, terminal 28) does not rise to 24 V within WTG parameter "Press.decr. blade bear.lubr. time" (wire break at the digital input, feeder blocked, mechanical fault in the switch) - pump is not permanently activated via the digital output "Request lubrication pump 2" (digital output QX5.14, main box, module 4, DIO232, terminal 14) (external potential at digital output, switching parameters incorrectly set, no power supply for pump) - various pump hardware errors | Inform the master service technician. A service call must be initiated within the time specified in the WTG parameter "Max.fail. blade bear.lubr.", as the WTG will otherwise be stopped automatically. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 72
13833 | 12021 | Max. time press. red. bl.bear. lubr. pump 3 | Blades | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Activation of the blade lubrication pump by the HC on axis 3 does not confirm a successful pressure reduction within the expected time (WTG parameter "Press.decr. blade bear.lubr. time") and thus a successful lubrication interval. This can have the following causes: - signal at digital input "End cycle lubr.pump 3" (digital input IX4.28, main box, module 4, DI232, terminal 28) does not rise to 24 V within WTG parameter "Press.decr. blade bear.lubr. time" (wire break at the digital input, feeder blocked, mechanical fault in the switch) - pump is not permanently activated via the digital output "Request lubrication pump 3" (digital output QX5.15, main box, module 4, DIO232, terminal 15) (external potential at digital output, switching parameters incorrectly set, no power supply for pump) - various pump hardware errors | Inform the responsible foreman. A service call must be initiated within the amount of time specified in the WTG parameter "Max.fail. blade bear.lubr.", since the WTG will otherwise be stopped automatically. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 73
13901 | 12022 | Vane pos. lim. switch 91° bl. 1 | Blades | WROT | Error | No |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Covert | See only | The rotor blade has moved itself out of the limit switch or the limit switch is defective. The digital input "91° limit switch blade 1" (digital input IX4.7, main box, module 4, DI232, terminal 7) carries 0V. | Initiate a service call. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 74
13902 | 12023 | Vane pos. lim. switch 91° bl. 2 | Blades | WROT | Error | No |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Covert | See only | The rotor blade has moved itself out of the limit switch or the limit switch is defective. The digital input "91° limit switch blade 2" (digital input IX4.8, main box, module 4, DI232, terminal 8) carries 0V. | Initiate a service call. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 75
13903 | 12024 | Vane pos. lim. switch 91° bl. 3 | Blades | WROT | Error | No |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Covert | See only | The rotor blade has moved itself out of the limit switch or the limit switch is defective. The digital input "91° limit switch blade 3" (digital input IX4.9, main box, module 4, DI232, terminal 9) carries 0V. | Initiate a service call. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 76
13910 | 12025 | Fault bypass limit switch | Blades | WROT | Error | Yes | *1s |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Covert | See only | The feedback at the digital input "No feedback bypass limit switch" (digital input IX4.30, main box, module 4, DI232, terminal 30) is not inverse to the request at digital output "Req. bypass lim. sw." (digital output QX5.16, main box, DIO232, terminal 16). A distinction is made between two cases: - Request of a bypass but no reaction of the system - Bypass of limit switch without request | Initiate a service call. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 77
12071 | 12051 | Maintenance switch battery 1 | Batteries | WROT | Info | Yes |  |  | Department | See only | Telenotdienst | See only | Covert | Covert | Covert | See only | The maintenance switch of the battery of axis 1 is open. The voltage supply from the batteries is interrupted. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 78
12072 | 12052 | Maintenance switch battery 2 | Batteries | WROT | Info | Yes |  |  | Department | See only | Telenotdienst | See only | Covert | Covert | Covert | See only | The maintenance switch of the battery of axis 2 is open. The voltage supply from the batteries is interrupted. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 79
12073 | 12053 | Maintenance switch battery 3 | Batteries | WROT | Info | Yes |  |  | Department | See only | Telenotdienst | See only | Covert | Covert | Covert | See only | The maintenance switch of the battery of axis 3 is open. The voltage supply from the batteries is interrupted. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 80
12081 | 12054 | Connection open battery 1 | Batteries | WROT | Info | Yes |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | The voltage supply from the battery of axis 1 is interrupted. Monitoring is performed via a signal contact in the plug connector of the rechargeable battery box. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 81
12082 | 12055 | Connection open battery 2 | Batteries | WROT | Info | Yes |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | The voltage supply from the battery of axis 2 is interrupted. Monitoring is performed via a signal contact in the plug connector of the rechargeable battery box. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 82
12083 | 12056 | Connection open battery 3 | Batteries | WROT | Info | Yes |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | The voltage supply from the battery of axis 3 is interrupted. Monitoring is performed via a signal contact in the plug connector of the rechargeable battery box. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 83
12101 | 12057 | Undervoltage battery 1 | Batteries | WROT | Warning | Yes | *1min |  | Department | See only | See only | Service and Maintenance | Covert | Covert | Covert | See only | The battery voltage monitor signals a low voltage of the battery of axis 1. The digital input "No undervoltage battery 1" (digital input IX4.13, main box, module 4, DI232, terminal 13) carries 0V. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 84
12102 | 12058 | Undervoltage battery 2 | Batteries | WROT | Warning | Yes | *1min |  | Department | See only | See only | Service and Maintenance | Covert | Covert | Covert | See only | The battery voltage monitor signals a low voltage of the battery of axis 2. The digital input "No undervoltage battery 2" (digital input IX4.14, main box, module 4, DI232, terminal 14) carries 0V. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 85
12103 | 12059 | Undervoltage battery 3 | Batteries | WROT | Warning | Yes | *1min |  | Department | See only | See only | Service and Maintenance | Covert | Covert | Covert | See only | The battery voltage monitor signals a low voltage of the battery of axis 3. The digital input "No undervoltage battery 3" (digital input IX4.15, main box, module 4, DI232, terminal 15) carries 0V. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 86
12111 | 12060 | Overvoltage battery 1 | Batteries | WROT | Info | No |  |  | Department | See only | See only | Service and Maintenance | Covert | Covert | Covert | See only | The battery voltage monitor signals a high voltage of the battery of axis 1. The digital input "No overvoltage battery 1" (digital input IX4.16, main box, module 4, DI232, terminal 16) carries 0V. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 87
12112 | 12061 | Overvoltage battery 2 | Batteries | WROT | Info | No |  |  | Department | See only | See only | Service and Maintenance | Covert | Covert | Covert | See only | The battery voltage monitor signals a high voltage of the battery of axis 2. The digital input "No overvoltage battery 2" (digital input IX4.17, main box, module 4, DI232, terminal 17) carries 0V. | Initiate a service call. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 88
12113 | 12062 | Overvoltage battery 3 | Batteries | WROT | Info | No |  |  | Department | See only | See only | Service and Maintenance | Covert | Covert | Covert | See only | The battery voltage monitor signals a high voltage of the battery of axis 3. The digital input "No overvoltage battery 3" (digital input IX4.18, main box, module 4, DI232, terminal 18) carries 0V. | Initiate a service call. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 89
12161 | 12063 | Meas. undervoltage battery 1 | Batteries | WROT | Warning | No | *1s |  | Department | See only | See only | Commissioning | Covert | Covert | Covert | See only | The voltage of battery 1 is too low. The minimum permissible voltage is defined in the "Min. battery voltage" parameter. The battery voltage monitor did not detect the undervoltage. | Initiate a service call. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 90
12162 | 12064 | Meas. undervoltage battery 2 | Batteries | WROT | Warning | No | *1s |  | Department | See only | See only | Commissioning | Covert | Covert | Covert | See only | The voltage of battery 2 is too low. The minimum permissible voltage is defined in the "Min. battery voltage" parameter. The battery voltage monitor did not detect the undervoltage. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 91
12163 | 12065 | Meas. undervoltage battery 3 | Batteries | WROT | Warning | No | *1s |  | Department | See only | See only | Commissioning | Covert | Covert | Covert | See only | The voltage of battery 3 is too low. The minimum permissible voltage is defined in the "Min. battery voltage" parameter. The battery voltage monitor did not detect the undervoltage. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 92
12171 | 12066 | Meas. overvoltage battery 1 | Batteries | WROT | Warning | No | *6s |  | Department | See only | See only | Commissioning | Covert | Covert | Covert | See only | The voltage of battery 1 is too high. The maximum permissible voltage is defined in the "Max. battery voltage" parameter. The battery voltage monitor did not detect the overvoltage. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 93
12172 | 12067 | Meas. overvoltage battery 2 | Batteries | WROT | Warning | No | *6s |  | Department | See only | See only | Commissioning | Covert | Covert | Covert | See only | The voltage of battery 2 is too high. The maximum permissible voltage is defined in the "Max. battery voltage" parameter. The battery voltage monitor did not detect the overvoltage. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 94
12173 | 12068 | Meas. overvoltage battery 3 | Batteries | WROT | Warning | No | *6s |  | Department | See only | See only | Commissioning | Covert | Covert | Covert | See only | The voltage of battery 3 is too high. The maximum permissible voltage is defined in the "Max. battery voltage" parameter. The battery voltage monitor did not detect the overvoltage. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 95
12201 | 12069 | High temperature battery 1 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of battery 1 is too high. The maximum permissible temperature is defined in the "Max. battery temperature" parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of battery 1 by comparing it with the temperature in the rotor hub. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 96
12202 | 12070 | High temperature battery 2 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of battery 2 is too high. The maximum permissible temperature is defined in the "Max. battery temperature" parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of battery 2 by comparing it with the temperature in the rotor hub. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 97
12203 | 12071 | High temperature battery 3 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of battery 3 is too high. The maximum permissible temperature is defined in the "Max. battery temperature" parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of battery 3 by comparing it with the temperature in the rotor hub. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 98
12211 | 12072 | Low temperature battery 1 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of battery 1 is too low. The minimum permissible temperature is defined in the "Min. battery temperature" parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in the rechargeable battery box has failed or temperature recognition is faulty. | Check the plausibility of the temperature of battery 1 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 99
12212 | 12073 | Low temperature battery 2 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of battery 2 is too low. The minimum permissible temperature is defined in the "Min. battery temperature" parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in the rechargeable battery box has failed or temperature recognition is faulty. | Check the plausibility of the temperature of battery 2 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 100
12213 | 12074 | Low temperature battery 3 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of battery 3 is too low. The minimum permissible temperature is defined in the "Min. battery temperature" parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in the rechargeable battery box has failed or temperature recognition is faulty. | Check the plausibility of the temperature of battery 3 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 101
12221 | 12075 | High temperature battery box 1 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of rechargeable battery box 1 is too high. The maximum permissible temperature is defined in the "Max. battery box temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of rechargeable battery box 1 by comparing it with the temperature in the rotor hub. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 102
12222 | 12076 | High temperature battery box 2 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of rechargeable battery box 2 is too high. The maximum permissible temperature is defined in the "Max. battery box temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of rechargeable battery box 2 by comparing it with the temperature in the rotor hub. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 103
12223 | 12077 | High temperature battery box 3 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of rechargeable battery box 3 is too high. The maximum permissible temperature is defined in the "Max. battery box temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of rechargeable battery box 3 by comparing it with the temperature in the rotor hub. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 104
12231 | 12078 | Low temperature battery box 1 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of rechargeable battery box 1 is too low. The minimum permissible temperature is defined in the "Min. battery box temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in the rechargeable battery box has failed or temperature recognition is faulty. | Check the plausibility of the temperature of rechargeable battery box 1 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 105
12232 | 12079 | Low temperature battery box 2 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of rechargeable battery box 2 is too low. The minimum permissible temperature is defined in the "Min. battery box temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in the rechargeable battery box has failed or temperature recognition is faulty. | Check the plausibility of the temperature of rechargeable battery box 2 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 106
12233 | 12080 | Low temperature battery box 3 | Batteries | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of rechargeable battery box 3 is too low. The minimum permissible temperature is defined in the "Min. battery box temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in the rechargeable battery box has failed or temperature recognition is faulty. | Check the plausibility of the temperature of rechargeable battery box 3 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 107
12241 | 12081 | High temp. abort charg. batt. 1 | Batteries | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | Pitch converter 1 is unable to charge the battery due to high battery temperature. Charging is aborted. | Check the temperature of the rechargeable battery box and the batteries and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 108
12242 | 12082 | High temp. abort charg. batt. 2 | Batteries | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | Pitch converter 2 is unable to charge the battery due to high battery temperature. Charging is aborted. | Check the temperature of the rechargeable battery box and the batteries and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 109
12243 | 12083 | High temp. abort charg. batt. 3 | Batteries | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | Pitch converter 3 is unable to charge the battery due to high battery temperature. Charging is aborted. | Check the temperature of the rechargeable battery box and the batteries and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 110
12250 | 12084 | Batt.box warm-up | Batteries | WROT | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | See only | Covert | Covert | See only | Following a grid failure or reboot of the hub controller, at least one of the battery boxes is warmed up due to low temperatures. | No reaction required. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 111
12251 | 12085 | Low temp. abort charg. batt. 1 | Batteries | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | Pitch converter 1 is unable to charge the battery because the battery temperature is too low. Charging is aborted. | Check the temperature of the rechargeable battery box and the batteries and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 112
12252 | 12086 | Low temp. abort charg. batt. 2 | Batteries | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | Pitch converter 2 is unable to charge the battery because the battery temperature is too low. Charging is aborted. | Check the temperature of the rechargeable battery box and the batteries and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 113
12253 | 12087 | Low temp. abort charg. batt. 3 | Batteries | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | Pitch converter 3 is unable to charge the battery because the battery temperature is too low. Charging is aborted. | Check the temperature of the rechargeable battery box and the batteries and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 114
12255 | 12088 | Batt.box temp. analysis | Batteries | WROT | Info | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | See only | Covert | Covert | See only | Following a grid failure or reboot of the hub controller, a check is made to determine whether the battery boxes must be warmed up due to low temperatures. | No reaction required. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 115
12260 | 12089 | Batt.box warm-up error | Batteries | WROT | Warning | No |  |  | Operation Control | See only | Telenotdienst | Commissioning | See only | Covert | Covert | See only | The hub controller's warm-up operation for at least one of the battery boxes was aborted due to an error. Manual restart of warm-up operation is currently possible. Possible causes: - desired battery box temperature is not reached - battery box temperature too high - sensor for battery box temperature defective - communication with pitch converters interrupted | Check for possible error status codes in Monitoring for the hub controller. As necessary, manually restart warm-up operation and check battery box temperature curve. Initiate a service call if necessary. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 116
12261 | 12090 | High temp. pause charge 1 | Batteries | WROT | Info | No |  |  | Department | See only |  | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | Pitch converter 1 is unable to charge the battery due to high battery temperature. Charging is paused. | No reaction required. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source) | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 117
12262 | 12091 | High temp. pause charge 2 | Batteries | WROT | Info | No |  |  | Department | See only |  | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | Pitch converter 2 is unable to charge the battery due to high battery temperature. Charging is paused. | No reaction required. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source) | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 118
12263 | 12092 | High temp. pause charge 3 | Batteries | WROT | Info | No |  |  | Department | See only |  | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | Pitch converter 3 is unable to charge the battery due to high battery temperature. Charging is paused. | No reaction required. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source) | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 119
12301 | 12093 | Error meas. temp. of batt. 1 | Batteries | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of battery 1. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 120
12302 | 12094 | Error meas. temp. of batt. 2 | Batteries | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of battery 2. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 121
12303 | 12095 | Error meas. temp. of batt. 3 | Batteries | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of battery 3. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 122
12321 | 12096 | Error meas.temp. of batt.box 1 | Batteries | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of rechargeable battery box 1. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 123
12322 | 12097 | Error meas.temp. of batt.box 2 | Batteries | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of rechargeable battery box 2. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 124
12323 | 12098 | Error meas.temp. of batt.box 3 | Batteries | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of rechargeable battery box 3. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 125
12371 | 12099 | Charging circuit fault batt. 1 | Batteries | WROT | Warning | Yes |  |  | Department | See only | See only | Commissioning | Covert | Covert | Covert | See only | Pitch converter 1 signals a fault of the charging circuit. Possible causes: - Battery temperature not ok - Charging current too high - Overvoltage / undervoltage of the battery | Check the voltage, charging current and temperature of the rechargeable battery and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 126
12372 | 12100 | Charging circuit fault batt. 2 | Batteries | WROT | Warning | Yes |  |  | Department | See only | See only | Commissioning | Covert | Covert | Covert | See only | Pitch converter 2 signals a fault of the charging circuit. Possible causes: - Battery temperature not ok - Charging current too high - Overvoltage / undervoltage of the battery | Check the voltage, charging current and temperature of the rechargeable battery and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 127
12373 | 12101 | Charging circuit fault batt. 3 | Batteries | WROT | Warning | Yes |  |  | Department | See only | See only | Commissioning | Covert | Covert | Covert | See only | Pitch converter 3 signals a fault of the charging circuit. Possible causes: - Battery temperature not ok - Charging current too high - Overvoltage / undervoltage of the battery | Check the voltage, charging current and temperature of the rechargeable battery and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 128
10202 | 12201 | Main box temp. high | Pitch | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature in main box A is too high. The maximum permissible temperature is defined in the "Max. main box temperature" parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature in main box A by comparing it with the temperature in the rotor hub. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 129
10212 | 12202 | Main box temp. low | Pitch | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature in main box A is too low. The minimum permissible temperature is defined in the "Min. main box temperature" parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in main box A has failed or temperature recognition is faulty. | Check the plausibility of the temperature in main box A by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 130
10250 | 12203 | Pitch back grid failure | Pitch | WROT | Error | Yes | *0 ms |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | At least one of the pitch converters reports a grid loss. After expiration of the SetDelay (UD), the control system of the WTG has not responded to it. Pitch back is triggered. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 131
10255 | 12204 | Rotor hub grid failure | Pitch | WROT | Info | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | At least one of the pitch converters reports a grid failure. The corresponding rotor blades are currently supplied with voltage by the batteries. | If the rotor hub reports a grid failure but the wind turbine does not, initiate a service call. Otherwise, no reaction required. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 132
10301 | 12205 | PT100 hub temp. defective | Pitch | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The PT100 is defective. The temperature measured at the input of the hub controller (analog input ID6.9, main box, module 8, GIO212, terminals 11+14) is lower than -80 °C or higher than +300 °C and therefore implausible. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 133
10302 | 12206 | PT100 main box defective | Pitch | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The PT100 is defective. The temperature measured at the input of the hub controller (analog input ID6.10, main box, module 6, GIO212, terminals 26+29) is lower than -80 °C or higher than +300 °C and therefore implausible. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 134
10311 | 12207 | Error meas. rotor hub temp. | Pitch | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature measured in the rotor hub (analog input ID6.9, main box, module 8, GIO212, terminals 11+14) does not change. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 135
10312 | 12208 | Error meas. temp. main box | Pitch | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature measured in main box A (analog input ID6.10, main box, module 6, GIO212, terminals 26+29) does not change. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 136
10400 | 12209 | Pitch warning | Pitch | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The digital input "No warning pitch" (digital input IX4.2, main box, module 4 (DI232), terminal 2) carries 0 V. The signal contacts of several fuses that are not absolutely necessary for the operation of the pitch system are located at this input. The protected devices are detailed in the current circuit diagram. This is just a warning. | Inform the responsible foreman that a service call is required as soon as possible. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 137
10404 | 12210 | Fault pitch axis 1 | Pitch | WROT | Error | Yes |  |  | SCADA User | See only |  | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | The pitch converter of axis 1 reports a fault of the pitch system. The devices of the respective signal chain can be found in the current circuit diagram. | Inform the responsible foreman that a service call is required as soon as possible. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source) | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 138
10405 | 12211 | Fault pitch axis 2 | Pitch | WROT | Error | Yes |  |  | SCADA User | See only |  | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | The pitch converter of axis 2 reports a fault of the pitch system. The devices of the respective signal chain can be found in the current circuit diagram. | Inform the responsible foreman that a service call is required as soon as possible. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source) | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 139
10406 | 12212 | Fault pitch axis 3 | Pitch | WROT | Error | Yes |  |  | SCADA User | See only |  | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | See only | The pitch converter of axis 3 reports a fault of the pitch system. The devices of the respective signal chain can be found in the current circuit diagram. | Inform the responsible foreman that a service call is required as soon as possible. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source) | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 140
10410 | 12213 | Overvoltage prot. Defective | Pitch | WROT | Error | Yes |  |  | Department | See only | Telenotdienst | Commissioning | Covert | Covert | Customer after warranty Professional | See only | The digital input "Overvoltage protection OK" (digital input IX4.22, main box, module 4, DI232, terminal 22) carries 0V. The overvoltage protection of the hub is defective. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 141
10440 | 12214 | Fault pitch main box | Pitch | WROT | Error | Yes |  |  | SCADA User | See only |  | Service and Maintenance | Troubleshooting | Covert | Ext. Service Provider | See only | Via the digital input "No error pitch main box" (digital input IX4.31, main box, module 4, DI232, terminal 31) of the hub controller, the pitch system reports an error in the main box. | Initiate a service call. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source) | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 142
10450 | 12215 | Hub service switch active | Pitch | WROT | Info | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The service switch in the hub is active (digital input IX4.21, main box, module 4, DI232, terminal 21). | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 143
10455 | 12216 | Service unit connected | Pitch | WROT | Info | Yes |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | A portable service unit for moving the rotor blades in manual operation is connected in the rotor hub (digital input IX5.25, main box, module 5, DIO232, terminal 25). | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 144
10460 | 12217 | Fault req. battery drive | Pitch | WROT | Error | Yes |  |  | Operation Control | See only | See only | Commissioning | Covert | Covert | Covert | See only | The feedback at digital input "Feedback req. battery drive HC" (digital input IX4.29, main box, module 4, DI232, terminal 29) is not inverse to the request at the digital output "No req. battery drive HC" (digital output QX5.4, main box, module 5, DI232, terminal 4). A distinction is made between two cases: - Request of a battery drive by the HC but no feedback of the corresponding contactor - Feedback of the contactor for triggering the battery drive by the HC, without corresponding request | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 145
10481 | 12218 | Fault act. batt.drive 1 | Pitch | WROT | Error | Yes |  |  | Department | See only |  | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | The pitch converter of axis 1 reports a fault in the actuation of the battery drive. | Initiate a service call. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source); service_partner: 'warramty' written as 'warranty' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 146
10482 | 12219 | Fault act. batt.drive 2 | Pitch | WROT | Error | Yes |  |  | Department | See only |  | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | The pitch converter of axis 2 reports a fault in the actuation of the battery drive. | Initiate a service call. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source); service_partner: 'warramty' written as 'warranty' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 147
10483 | 12220 | Fault act. batt.drive 3 | Pitch | WROT | Error | Yes |  |  | Department | See only |  | Service and Maintenance | Preventive Maintenance | Covert | Customer after warranty Professional | Advanced | The pitch converter of axis 3 reports a fault in the actuation of the battery drive. | Initiate a service call. | 3 |  | Test on proto | TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source); service_partner: 'warramty' written as 'warranty' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 148
13840 | 12221 | Hub fan error | Pitch | WROT | Warning | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | The optional rotor hub fan signals a warning via the digital input "Hub fan no warn." (digital input IX4.19, main box, module 4, DI232, terminal 19). This can have the following causes: - fan overload - incorrect or missing voltage supply to the fan - signal wiring error or cable break - activation of the "Sand & Dust" optional product on the WTG, although a fan is not installed in the rotor hub | Clarify whether the "Sand & Dust" option is installed on the WTG; check the WTG parameter "Sand&Dust act.". Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 149
13845 | 12222 | Hub fan manual mode | Pitch | WROT | Info | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Preventive Maintenance | Covert | Covert | Advanced | Manual operation is requested for the optional rotor hub fan. | If no service call is currently taking place: use the access list to clarify who activated manual operation and why it was activated. Deactivate manual operation if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 150
10000 | 12223 | Pitch back WTG | Pitch | WROT | Info | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | Pitch back is activated upon request from the wind turbine. The digital "Pitch Back inactive" signal (digital input IX4.20, main box, module 4, DI232, terminal 20) from the wind turbine control system via the slip ring has disappeared. This happens when brake program 170 is triggered. | Check the visualization of the wind turbine to find out what caused this. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 151
10010 | 12224 | Battery drive | Pitch | WROT | Info | No | *100ms |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | At least one of the pitch converters reports a battery drive. Battery drive is triggered. The pitch converters receive this information via a digital input that is controlled via the contactor for the battery drive. Normally, the battery drive should be triggered with brake programs 180 and higher. Otherwise, there is a malfunction. | Check the visualization of the wind turbine to find out what caused this. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 152
10020 | 12225 | Pitch back trigger by WTG | Pitch | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | The control of the WTG reports via the communication interface that it initiates a pitch back. | Check the visualization of the wind turbine to find out what caused this. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 153
10025 | 12226 | Battery drive trigger by WTG | Pitch | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | The control of the WTG reports via the communication interface that it initiates a battery drive. | Check the visualization of the wind turbine to find out what caused this. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 154
10030 | 12227 | Assembly mode | Pitch | WROT | Info | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | Assembly mode is active. If this status code occurs in the field, the wrong parameter file has been loaded. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 155
10050 | 12228 | Repeated error | Pitch | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | Repeated error with stop program 0. Used for notification in case of an especially frequent warning. | Observe the instructions for the respective fault. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 156
10060 | 12229 | Trigger snapshot by WTG | Pitch | WROT | Info | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | See only | Covert | Ext. Service Provider | See only | The control of the WTG reports via the communication interface that it records a snapshot. For validation and analysis purposes, a snapshot is recorded in parallel by the hub controller. | No reaction required. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 157
10065 | 12230 | Max. stop time SP40 | Pitch | WROT | Error | No | *80s |  | Operation Control | See only | Telenotdienst | See only | Covert | Covert | Covert | See only | Pitch back was not ended properly within the time defined by the status code's SetDelay. Possible reasons: At least one of the angle setpoints for the rotor blades provided by the wind turbine is 89 ° or smaller (control system of the wind turbine does not respond correctly or communication between the system and the hub controller is interrupted). At least one of the 91 ° limit switches is faulty. At least one rotor blade could not be moved as desired. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 158
10070 | 12231 | Max. stop time SP80 | Pitch | WROT | Error | No | *80s |  | Operation Control | See only | Telenotdienst | See only | Covert | Covert | Covert | See only | A battery drive was not ended properly within the time defined by the status code's SetDelay. Possible reasons: At least one of the angle setpoints for the rotor blades provided by the wind turbine is 89 ° or smaller (control system of the wind turbine does not respond correctly or communication between the system and the hub controller is interrupted). At least one of the 91 ° limit switches is faulty. At least one rotor blade could not be moved as desired. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 159
10075 | 12232 | SP40 speed error | Pitch | WROT | Error | Yes |  |  | Operation Control | See only | See only | See only | Covert | Covert | See only | See only | Braking program 40 is active and at least one axis, the pitch speed is not within the limits defined by the parameters "SP40 min. actual pitch rate" and "SP40 max. actual pitch rate". Possible causes: - Mechanical problems (such as, engaged brake or sluggishness of blade pitch mechanical elements. Check pitch motor currents.) - B encoder defective - For pitch back during grid loss: battery of an axis too weak | Initiate a service call | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 160
10080 | 12233 | SP80 speed error | Pitch | WROT | Error | Yes |  |  | Operation Control | See only | See only | See only | Covert | Covert | See only | See only | Braking program 80 is active and at least one axis, the pitch speed is not within the limits defined by the parameters "SP80 min. actual pitch rate" and "SP80 max. actual pitch rate". Possible causes: - Mechanical problems (such as, engaged brake or sluggishness of blade pitch mechanical elements. Check pitch motor currents.) - B encoder defective - For battery drive during grid loss: battery of an axis too weak | Initiate a service call | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 161
10085 | 12234 | Test stop program 40 | Pitch | WROT | Info | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | A test for stop program 40 was requested in the visualization of the hub controller. | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 162
10090 | 12235 | Test stop program 80 | Pitch | WROT | Info | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | A test for stop program 80 was requested in the visualization of the hub controller. | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 163
11110 | 12251 | Blade coll. setp. Implausible | Pitch Control | WROT | Error | No |  |  | Operation Control | See only | See only | Commissioning | See only | Covert | See only | See only | The blade-collective setpoint average of the three blades averaged over 50 ms is outside a plausible limit value range. This may be triggered by incorrect parametrization of the limits or a serious software error. | Shut down the WTG and inform SCADA Control Engineering Development. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 164
11120 | 12252 | Max. blade indiv. angle setpoint rate | Pitch Control | WROT | Error | No |  |  | Department | See only |  | Service and Maintenance | See only | Covert | See only | See only | For at least one of the 3 pitch angle setpoints determined by the WTG control system, exceeding the maximum permissible limit values of the rates of change was detected, either in the positive or negative direction. | If this error occurs more frequently: Shut down the WTG and inform SCADA Control Engineering Development. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only'; TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source) | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 165
11130 | 12253 | Max. blade coll. angle setpoint rate | Pitch Control | WROT | Error | No |  |  | Department | See only |  | Service and Maintenance | See only | Covert | See only | See only | For the collective pitch angle setpoint (formed from the 3 individual pitch angle setpoints determined by the WTG control system), a too great deviation (parameterized with "Blade coll. setp. tol. test dev.") to the rate limited check pitch angle was detected. | If this error occurs more frequently: Shut down the WTG and inform SCADA Control Engineering Development. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only'; TCC access in the source: 'Covert' (the TCC lookup has no such level; left empty - add the level to the lookup or correct the source) | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 166
11140 | 12254 | Max. blade indiv. setp.angle dev. | Pitch Control | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | See only | Covert | Covert | See only | For one of the 3 individual pitch angle setpoints determined by the WTG control system and the collective setpoint calculated from them, a too great deviation (parameterized with "Max. blade indiv. setp.dev.") was identified. | If this error occurs more frequently: Shut down the WTG and inform SCADA Control Engineering Development. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 167
11150 | 12255 | Max. setp.angle offset TFL | Pitch Control | WROT | Error | Yes | *100ms |  | Department | See only | PMS Dispatcher | Service and Maintenance | See only | Covert | Covert | See only | The "TFL setp.angle offset" transmitted from the WTG controller to the hub controller has assumed an implausible value that is too high. This indicates a software error in the WTG controller. | Shut down the WTG and inform SCADA control engineering development department. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 168
11155 | 12256 | Max. setp. offset DTC | Pitch Control | WROT | Error | Yes | *100ms |  | Department | See only | PMS Dispatcher | Service and Maintenance | See only | Covert | Covert | See only | The "Blade angle setpoint offset DTC" transmitted from the WTG controller to the hub controller has assumed an implausible value that is too high. This indicates a software error in the WTG controller. | Shut down the WTG and inform SCADA control engineering development department. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 169
11301 | 12257 | Incorrect pitch ramp parameter | Pitch Control | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | See only | Covert | Covert | See only | The "pitch ramp" control function is not parameterized correctly. | Initiate a service call. Load the correct parameter file. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 170
11302 | 12258 | Incorrect controller parameter | Pitch Control | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The "controller" control function is not parameterized correctly. | Initiate a service call. Load the correct parameter file. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 171
11303 | 12259 | Incorr. pitch rate funct. param. | Pitch Control | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The "pitch rate function" control function is not parameterized correctly. | Initiate a service call. Load the correct parameter file. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 172
13201 | 12301 | High temperature pt. mot. 1 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch motor 1 is too high. The maximum permissible temperature is defined in the "Max. pitch motor temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". Possible causes: - Fan or blade pitch mechanics problem (see WTI 84) - Sensor faulty (implausible measured values, e.g., temperature extremely high/low or great increase in the measured values) | Check whether the temperature is plausible or whether high currents may be the reason. The pitch motors warm up to 100 °C during normal operation. Temperatures of approx. 150 °C are critical for the motor. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 173
13202 | 12302 | High temperature pt. mot. 2 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch motor 2 is too high. The maximum permissible temperature is defined in the "Max. pitch motor temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". Possible causes: - Fan or blade pitch mechanics problem (see WTI 84) - Sensor faulty (implausible measured values, e.g., temperature extremely high/low or great increase in the measured values) | Check whether the temperature is plausible or whether high currents may be the reason. The pitch motors warm up to 100 °C during normal operation. Temperatures of approx. 150 °C are critical for the motor. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 174
13203 | 12303 | High temperature pt. mot. 3 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch motor 3 is too high. The maximum permissible temperature is defined in the "Max. pitch motor temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". Possible causes: - Fan or blade pitch mechanics problem (see WTI 84) - Sensor faulty (implausible measured values, e.g., temperature extremely high/low or great increase in the measured values) | Check whether the temperature is plausible or whether high currents may be the reason. The pitch motors warm up to 100 °C during normal operation. Temperatures of approx. 150 °C are critical for the motor. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 175
13211 | 12304 | Low temperature pitch motor 1 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch motor 1 is too low. The minimum permissible temperature is defined in the "Min. pitch motor temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating of the pitch motor has failed or temperature recognition is faulty. | Check the plausibility of the temperature of pitch motor 1 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 176
13212 | 12305 | Low temperature pitch motor 2 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch motor 2 is too low. The minimum permissible temperature is defined in the "Min. pitch motor temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating of the pitch motor has failed or temperature recognition is faulty. | Check the plausibility of the temperature of pitch motor 2 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 177
13213 | 12306 | Low temperature pitch motor 3 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch motor 3 is too low. The minimum permissible temperature is defined in the "Min. pitch motor temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating of the pitch motor has failed or temperature recognition is faulty. | Check the plausibility of the temperature of pitch motor 3 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 178
13221 | 12307 | High temp.blade pitch gearb. 1 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of blade pitch gearbox 1 is too high. The maximum permissible temperature is defined in the "Max. pitch gearbox temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of blade pitch gearbox 1. Initiate a service call if necessary. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 179
13222 | 12308 | High temp.blade pitch gearb. 2 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of blade pitch gearbox 2 is too high. The maximum permissible temperature is defined in the "Max. pitch gearbox temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of blade pitch gearbox 2. Initiate a service call if necessary. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 180
13223 | 12309 | High temp.blade pitch gearb. 3 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of blade pitch gearbox 3 is too high. The maximum permissible temperature is defined in the "Max. pitch gearbox temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of blade pitch gearbox 3. Initiate a service call if necessary. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 181
13231 | 12310 | Low temp.blade pitch gearb. 1 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of blade pitch gearbox 1 is too low. The minimum permissible temperature is defined in the "Min. pitch gearbox temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. | Check the plausibility of the temperature of blade pitch gearbox 1 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 182
13232 | 12311 | Low temp.blade pitch gearb. 2 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of blade pitch gearbox 2 is too low. The minimum permissible temperature is defined in the "Min. pitch gearbox temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. | Check the plausibility of the temperature of blade pitch gearbox 2 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 183
13233 | 12312 | Low temp.blade pitch gearb. 3 | Pitch drives | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of blade pitch gearbox 3 is too low. The minimum permissible temperature is defined in the "Min. pitch gearbox temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. | Check the plausibility of the temperature of blade pitch gearbox 3 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 184
13301 | 12313 | Error meas. temp. of pt.mot. 1 | Pitch drives | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of pitch motor 1. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 185
13302 | 12314 | Error meas. temp. of pt.mot. 2 | Pitch drives | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of pitch motor 2. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 186
13303 | 12315 | Error meas. temp. of pt.mot. 3 | Pitch drives | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of pitch motor 3. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 187
13321 | 12316 | Error meas.temp. of pt.gearb.1 | Pitch drives | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of blade pitch gearbox 1 is too low. The minimum permissible temperature is defined in the "Min. pitch gearbox temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. | Check the plausibility of the temperature of blade pitch gearbox 1 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 188
13322 | 12317 | Error meas.temp. of pt.gearb.2 | Pitch drives | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of blade pitch gearbox 2 is too low. The minimum permissible temperature is defined in the "Min. pitch gearbox temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. | Check the plausibility of the temperature of blade pitch gearbox 2 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 189
13323 | 12318 | Error meas.temp. of pt.gearb.3 | Pitch drives | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of blade pitch gearbox 3 is too low. The minimum permissible temperature is defined in the "Min. pitch gearbox temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. | Check the plausibility of the temperature of blade pitch gearbox 3 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. The wind turbine can remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 190
13371 | 12319 | 4-20mA curr.sensor pt. mot. 1 | Pitch drives | WROT | Error | Yes |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The sensor of the pitch converter of axis 1 for recording the corresponding pitch motor current, or the pitch converter cabling, is defective. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 191
13372 | 12320 | 4-20mA curr.sensor pt. mot. 2 | Pitch drives | WROT | Error | Yes |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The sensor of the pitch converter of axis 2 for recording the corresponding pitch motor current, or the pitch converter cabling, is defective. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 192
13373 | 12321 | 4-20mA curr.sensor pt. mot. 3 | Pitch drives | WROT | Error | Yes |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The sensor of the pitch converter of axis 3 for recording the corresponding pitch motor current, or the pitch converter cabling, is defective. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 193
13421 | 12322 | Error shunt current pt. mot. 1 | Pitch drives | WROT | Error | No |  |  | Department | See only | Telenotdienst | Commissioning | Covert | Covert | Covert | See only | Pitch converter 1 signals an error of the shunt winding of the pitch motor. The current level is too low. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 194
13422 | 12323 | Error shunt current pt. mot. 2 | Pitch drives | WROT | Error | No |  |  | Department | See only | Telenotdienst | Commissioning | Covert | Covert | Covert | See only | Pitch converter 2 signals an error of the shunt winding of the pitch motor. The current level is too low. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 195
13423 | 12324 | Error shunt current pt. mot. 3 | Pitch drives | WROT | Error | No |  |  | Department | See only | Telenotdienst | Commissioning | Covert | Covert | Covert | See only | Pitch converter 3 signals an error of the shunt winding of the pitch motor. The current level is too low. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 196
13451 | 12325 | Error bridging start resistor 1 | Pitch drives | WROT | Error | No | *2500ms |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | During a battery drive, the pitch motor current is reduced by a resistor during start-up. After the battery drive has started, the resistor is bridged by a contactor. If the corresponding contactor of axis 1 does not switch, the status code is activated. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 197
13452 | 12326 | Error bridging start resistor 2 | Pitch drives | WROT | Error | No | *2500ms |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | During a battery drive, the pitch motor current is reduced by a resistor during start-up. After the battery drive has started, the resistor is bridged by a contactor. If the corresponding contactor of axis 2 does not switch, the status code is activated. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 198
13453 | 12327 | Error bridging start resistor 3 | Pitch drives | WROT | Error | No | *2500ms |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | During a battery drive, the pitch motor current is reduced by a resistor during start-up. After the battery drive has started, the resistor is bridged by a contactor. If the corresponding contactor of axis 3 does not switch, the status code is activated. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 199
13471 | 12328 | Fuse external fan pt. mot. 1 | Pitch drives | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The fuse of the external fan of pitch motor 1 has triggered. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 200
13472 | 12329 | Fuse external fan pt. mot. 2 | Pitch drives | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The fuse of the external fan of pitch motor 2 has triggered. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 201
13473 | 12330 | Fuse external fan pt. mot. 3 | Pitch drives | WROT | Warning | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The fuse of the external fan of pitch motor 3 has triggered. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 202
13481 | 12331 | Error pitch brake 1 | Pitch drives | WROT | Error | No |  |  | Department | See only | Telenotdienst | Commissioning | Covert | Covert | Covert | See only | Pitch converter 1 signals an error when opening the pitch motor brake. Possible causes: - Short circuit or cable break in the electric circuit of the pitch motor brake - Contactor for emergency control of the brake does not send feedback in the event of an unregulated battery drive The pitch converter remains ready for operation. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 203
13482 | 12332 | Error pitch brake 2 | Pitch drives | WROT | Error | No |  |  | Department | See only | Telenotdienst | Commissioning | Covert | Covert | Covert | See only | Pitch converter 2 signals an error when opening the pitch motor brake. Possible causes: - Short circuit or cable break in the electric circuit of the pitch motor brake - Contactor for emergency control of the brake does not send feedback in the event of an unregulated battery drive The pitch converter remains ready for operation. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 204
13483 | 12333 | Error pitch brake 3 | Pitch drives | WROT | Error | No |  |  | Department | See only | Telenotdienst | Commissioning | Covert | Covert | Covert | See only | Pitch converter 3 signals an error when opening the pitch motor brake. Possible causes: - Short circuit or cable break in the electric circuit of the pitch motor brake - Contactor for emergency control of the brake does not send feedback in the event of an unregulated battery drive The pitch converter remains ready for operation. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 205
12501 | 12401 | No RFO pitch converter 1 | Pitch converter | WROT | Error | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The RFO signal (= ready for operation) of pitch converter 1 disappeared. The pitch converter reports a major fault, e.g., fan faulty, grid error, parameter error, batteries not connected, CAN bus error, DC link diode fault or an error of the pitch converter or its control system. | Check whether additional status codes have occurred that might explain the missing RFO signal. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 206
12502 | 12402 | No RFO pitch converter 2 | Pitch converter | WROT | Error | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The RFO signal (= ready for operation) of pitch converter 2 disappeared. The pitch converter reports a major fault, e.g., fan faulty, grid error, parameter error, batteries not connected, CAN bus error, DC link diode fault or an error of the pitch converter or its control system. | Check whether additional status codes have occurred that might explain the missing RFO signal. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 207
12503 | 12403 | No RFO pitch converter 3 | Pitch converter | WROT | Error | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The RFO signal (= ready for operation) of pitch converter 3 disappeared. The pitch converter reports a major fault, e.g., fan faulty, grid error, parameter error, batteries not connected, CAN bus error, DC link diode fault or an error of the pitch converter or its control system. | Check whether additional status codes have occurred that might explain the missing RFO signal. Initiate a service call if necessary. | 1 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 208
12511 | 12404 | No feedback pitch converter 1 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 1 could not be activated or deactivated completely within the specified time. If the pitch converter was activated, not all of the expected feedbacks from the pitch converter were received within in the time defined in "Time feedb. act. pt. conv." For successful activation, the following feedbacks are required: - The corresponding control contactor must be active, i.e., "Feedb. norm. op. pt. conv. 1" must be active. - Enable controller must be acknowledged, i.e., "Feedb. en. ctrl. pt. conv. 1" must be active. - Enable pitch motor must be acknowledged, i.e. "Feedb. pt.mot.en. pt.conv. 1" must be active. If the pitch converter was deactivated, not all expected feedbacks from the pitch converter were available within the time defined in "Time feedb. deact. pt. conv." The following feedbacks are required for successful deactivation: - The cancellation of enable pitch motor must be acknowledged, i.e., "Feedb. pt.mot.en. pt.conv. 1" must be inactive. - The cancellation of enable controller must be acknowledged, i.e., "Feedb. en. ctrl. pt. conv. 1" must be inactive. | Initiate a service call. | 1 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 209
12512 | 12405 | No feedback pitch converter 2 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 2 could not be activated or deactivated completely within the specified time. If the pitch converter was activated, not all of the expected feedbacks from the pitch converter were received within in the time defined in "Time feedb. act. pt. conv." For successful activation, the following feedbacks are required: - The corresponding control contactor must be active, i.e., "Feedb. norm. op. pt. conv. 2" must be active. - Enable controller must be acknowledged, i.e., "Feedb. en. ctrl. pt. conv. 2" must be active. - Enable pitch motor must be acknowledged, i.e. "Feedb. pt.mot.en. pt.conv. 2" must be active. If the pitch converter was deactivated, not all expected feedbacks from the pitch converter were available within the time defined in "Time feedb. deact. pt. conv." The following feedbacks are required for successful deactivation: - The cancellation of enable pitch motor must be acknowledged, i.e., "Feedb. pt.mot.en. pt.conv. 2" must be inactive. - The cancellation of enable controller must be acknowledged, i.e., "Feedb. en. ctrl. pt. conv. 2" must be inactive. | Initiate a service call. | 1 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 210
12513 | 12406 | No feedback pitch converter 3 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 3 could not be activated or deactivated completely within the specified time. If the pitch converter was activated, not all of the expected feedbacks from the pitch converter were received within in the time defined in "Time feedb. act. pt. conv." For successful activation, the following feedbacks are required: - The corresponding control contactor must be active, i.e., "Feedb. norm. op. pt. conv. 3" must be active. - Enable controller must be acknowledged, i.e., "Feedb. en. ctrl. pt. conv. 3" must be active. - Enable pitch motor must be acknowledged, i.e. "Feedb. pt.mot.en. pt.conv. 3" must be active. If the pitch converter was deactivated, not all expected feedbacks from the pitch converter were available within the time defined in "Time feedb. deact. pt. conv." The following feedbacks are required for successful deactivation: - The cancellation of enable pitch motor must be acknowledged, i.e., "Feedb. pt.mot.en. pt.conv. 3" must be inactive. - The cancellation of enable controller must be acknowledged, i.e., "Feedb. en. ctrl. pt. conv. 3" must be inactive. | Initiate a service call. | 1 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 211
12561 | 12407 | Grid failure timeout pt.conv. 1 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 1 reports a grid loss that is longer than the parameterized timeout duration. If this is the case, the pitch converter is no longer ready for operation and the pitch converter RFO signal disappears. | If a general grid failure has occurred, there is no need for action. Otherwise initiate a service call. | 1 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 212
12562 | 12408 | Grid failure timeout pt.conv. 2 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 2 reports a grid loss that is longer than the parameterized timeout duration. If this is the case, the pitch converter is no longer ready for operation and the pitch converter RFO signal disappears. | If a general grid failure has occurred, there is no need for action. Otherwise initiate a service call. | 1 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 213
12563 | 12409 | Grid failure timeout pt.conv. 3 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 3 reports a grid loss that is longer than the parameterized timeout duration. If this is the case, the pitch converter is no longer ready for operation and the pitch converter RFO signal disappears. | If a general grid failure has occurred, there is no need for action. Otherwise initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 214
12621 | 12410 | DC link volt. low pt. conv. 1 | Pitch converter | WROT | Info | No | *500ms |  | Department | See only | See only | Service and Maintenance | Covert | Covert | Covert | See only | The DC link voltage of pitch converter 1 is too low. The minimum permissible voltage is defined in the "Min. DC-link pt. conv. volt." parameter. | Check the DC link voltage and initiate a service call if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 215
12622 | 12411 | DC link volt. low pt. conv. 2 | Pitch converter | WROT | Info | No | *500ms |  | Department | See only | See only | Service and Maintenance | Covert | Covert | Covert | See only | The DC link voltage of pitch converter 2 is too low. The minimum permissible voltage is defined in the "Min. DC-link pt. conv. volt." parameter. | Check the DC link voltage and initiate a service call if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 216
12623 | 12412 | DC link volt. low pt. conv. 3 | Pitch converter | WROT | Info | No | *500ms |  | Department | See only | See only | Service and Maintenance | Covert | Covert | Covert | See only | The DC link voltage of pitch converter 3 is too low. The minimum permissible voltage is defined in the "Min. DC-link pt. conv. volt." parameter. | Check the DC link voltage and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 217
12701 | 12413 | High temp. pitch converter 1 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter 1 is too high. The maximum permissible temperature is defined in the "Max. pitch converter temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of pitch converter 1 by comparing it with the temperature in the rotor hub. Check whether high currents might be the reason for the increase in temperature. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 218
12702 | 12414 | High temp. pitch converter 2 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter 2 is too high. The maximum permissible temperature is defined in the "Max. pitch converter temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of pitch converter 2 by comparing it with the temperature in the rotor hub. Check whether high currents might be the reason for the increase in temperature. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 219
12703 | 12415 | High temp. pitch converter 3 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter 3 is too high. The maximum permissible temperature is defined in the "Max. pitch converter temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of pitch converter 3 by comparing it with the temperature in the rotor hub. Check whether high currents might be the reason for the increase in temperature. If the temperature is not plausible, inform TCC Level 2 if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 220
12711 | 12416 | Low temp. pitch converter 1 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter 1 is too low. The minimum permissible temperature is defined in the "Min. pitch converter temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating of the pitch converter has failed or temperature recognition is faulty. | Check the plausibility of the temperature of pitch converter 1 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 221
12712 | 12417 | Low temp. pitch converter 2 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter 2 is too low. The minimum permissible temperature is defined in the "Min. pitch converter temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating of the pitch converter has failed or temperature recognition is faulty. | Check the plausibility of the temperature of pitch converter 2 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 222
12713 | 12418 | Low temp. pitch converter 3 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter 3 is too low. The minimum permissible temperature is defined in the "Min. pitch converter temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating of the pitch converter has failed or temperature recognition is faulty. | Check the plausibility of the temperature of pitch converter 3 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 223
12721 | 12419 | High temp. pt. conv. box 1 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter box 1 is too high. The maximum permissible temperature is defined in the "Max. pt. conv. box temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of pitch converter box 1 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 224
12722 | 12420 | High temp. pt. conv. box 2 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter box 2 is too high. The maximum permissible temperature is defined in the "Max. pt. conv. box temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of pitch converter box 2 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 225
12723 | 12421 | High temp. pt. conv. box 3 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter box 3 is too high. The maximum permissible temperature is defined in the "Max. pt. conv. box temp." parameter. The status code is only reset if the temperature falls below this maximum temperature by the value defined in "Temperature diff. reset". | Check the plausibility of the temperature of pitch converter box 3 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 226
12731 | 12422 | Low temp. pt. conv. box 1 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter box 1 is too low. The minimum permissible temperature is defined in the "Min. pt. conv. box temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in the pitch converter box has failed or temperature recognition is faulty. | Check the plausibility of the temperature of pitch converter box 1 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 227
12732 | 12423 | Low temp. pt. conv. box 2 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter box 2 is too low. The minimum permissible temperature is defined in the "Min. pt. conv. box temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in the pitch converter box has failed or temperature recognition is faulty. | Check the plausibility of the temperature of pitch converter box 2 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 228
12733 | 12424 | Low temp. pt. conv. box 3 | Pitch converter | WROT | Error | No |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | The temperature of pitch converter box 3 is too low. The minimum permissible temperature is defined in the "Min. pt. conv. box temp." parameter. The status code is only reset if the temperature exceeds this minimum temperature by the value defined in "Temperature diff. reset".. The heating in the pitch converter box has failed or temperature recognition is faulty. | Check the plausibility of the temperature of pitch converter box 3 by comparing it with the temperature in the rotor hub. Initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 229
12801 | 12425 | Error meas.temp. of pt.conv. 1 | Pitch converter | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of pitch converter 1. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 230
12802 | 12426 | Error meas.temp. of pt.conv. 2 | Pitch converter | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of pitch converter 2. | Check the temperature and initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 231
12803 | 12427 | Error meas.temp. of pt.conv. 3 | Pitch converter | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of pitch converter 3. | Check the temperature and initiate a service call if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 232
12821 | 12428 | Err.meas.temp.of pt.conv.box1 | Pitch converter | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of pitch converter box 1. | Check the temperature and initiate a service call if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 233
12822 | 12429 | Err.meas.temp.of pt.conv.box2 | Pitch converter | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of pitch converter box 2. | Check the temperature and initiate a service call if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 234
12823 | 12430 | Err.meas.temp.of pt.conv.box3 | Pitch converter | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | Covert | Covert | Covert | See only | An error occurred while measuring the temperature of pitch converter box 3. | Check the temperature and initiate a service call if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 235
12851 | 12431 | Warning pitch converter 1 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 1 signals an error. Operation is still possible. This is just a warning. Details are available in the documentation of the pitch converter. | Inform the responsible foreman that a service call is required as soon as possible. The wind turbine may remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 236
12852 | 12432 | Warning pitch converter 2 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 2 signals an error. Operation is still possible. This is just a warning. Details are available in the documentation of the pitch converter. | Inform the responsible foreman that a service call is required as soon as possible. The wind turbine may remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 237
12853 | 12433 | Warning pitch converter 3 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 3 signals an error. Operation is still possible. This is just a warning. Details are available in the documentation of the pitch converter. | Inform the responsible foreman that a service call is required as soon as possible. The wind turbine may remain in operation until servicing is carried out. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 238
12861 | 12434 | DC link diode faulty pt. conv. 1 | Pitch converter | WROT | Warning | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The DC link diode of pitch converter 1 is faulty. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 239
12862 | 12435 | DC link diode faulty pt. conv. 2 | Pitch converter | WROT | Warning | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The DC link diode of pitch converter 2 is faulty. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | nitiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 240
12863 | 12436 | DC link diode faulty pt. conv. 3 | Pitch converter | WROT | Warning | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The DC link diode of pitch converter 3 is faulty. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 241
12871 | 12437 | DO short circuit pt. conv. 1 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 1 reports a short circuit at one of the digital outputs. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 242
12872 | 12438 | DO short circuit pt. conv. 2 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 2 reports a short circuit at one of the digital outputs. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 243
12873 | 12439 | DO short circuit pt. conv. 3 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | Pitch converter 3 reports a short circuit at one of the digital outputs. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 244
12881 | 12440 | No RFO chopper pt. conv. 1 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | The chopper resistor of pitch converter 1 is not ready for operation. If the rotor blades are powered by the wind during a battery drive, the excess energy is "burned" via the chopper resistor. The status becomes active if the resistor was overloaded or too much voltage is present. | Check in which operating state the error occurred. If a large number of battery drives have been performed in a row, the wind turbine can be restarted after a cool-down period. Otherwise initiate a service call if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 245
12882 | 12441 | No RFO chopper pt. conv. 2 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | The chopper resistor of pitch converter 2 is not ready for operation. If the rotor blades are powered by the wind during a battery drive, the excess energy is "burned" via the chopper resistor. The status becomes active if the resistor was overloaded or too much voltage is present. | Check in which operating state the error occurred. If a large number of battery drives have been performed in a row, the wind turbine can be restarted after a cool-down period. Otherwise initiate a service call if necessary. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 246
12883 | 12442 | No RFO chopper pt. conv. 3 | Pitch converter | WROT | Warning | No |  |  | Department | See only | See only | See only | Covert | Covert | Covert | See only | The chopper resistor of pitch converter 3 is not ready for operation. If the rotor blades are powered by the wind during a battery drive, the excess energy is "burned" via the chopper resistor. The status becomes active if the resistor was overloaded or too much voltage is present. | Check in which operating state the error occurred. If a large number of battery drives have been performed in a row, the wind turbine can be restarted after a cool-down period. Otherwise initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 247
12891 | 12443 | Chopper overload pt. conv. 1 | Pitch converter | WROT | Error | Yes |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The chopper resistor of pitch converter 1 is overloaded. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. If the rotor blades are powered by the wind during a battery drive, the excess energy is "burned" via the chopper resistor. | Check in which operating state the error occurred. If a large number of battery drives have been performed in a row, the wind turbine can be restarted after a cool-down period. Otherwise initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 248
12892 | 12444 | Chopper overload pt. conv. 2 | Pitch converter | WROT | Error | Yes |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The chopper resistor of pitch converter 2 is overloaded. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. If the rotor blades are powered by the wind during a battery drive, the excess energy is "burned" via the chopper resistor. | Check in which operating state the error occurred. If a large number of battery drives have been performed in a row, the wind turbine can be restarted after a cool-down period. Otherwise initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 249
12893 | 12445 | Chopper overload pt. conv. 3 | Pitch converter | WROT | Error | Yes |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The chopper resistor of pitch converter 3 is overloaded. If this is the case, the pitch converter is no longer operational and the pitch converter RFO signal disappears. If the rotor blades are powered by the wind during a battery drive, the excess energy is "burned" via the chopper resistor. | Check in which operating state the error occurred. If a large number of battery drives have been performed in a row, the wind turbine can be restarted after a cool-down period. Otherwise initiate a service call if necessary. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 250
14000 | 12501 | Rotor overspeed | Rotor | WROT | Error | No | *450ms |  | See only | See only | See only | See only | Covert | Covert | Covert | See only | A rotor overspeed was detected by the hub controller. A battery drive is triggered. Possible causes: - Strong gust of wind - Measurement error - Pitch system malfunction - Load shedding (e.g., due to grid failure, tripping of the main switch) - Coupling slipped (gearbox speed higher than generator speed) | Check the wind data, pitch angles and all speeds in the snapshot of the wind turbine control system and check the status code list. If the overspeed occurred only briefly and was caused by a gust of wind, load shedding or a measurement error, the wind turbine can be restarted. In the case of other causes or repeated occurrences, initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 251
14005 | 12502 | Rotor overspeed test | Rotor | WROT | Info | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | A rotor overspeed test was requested in the visualization of the hub controller. | If the user has not identified himself by logging in or registering with PMS: Clarify who is at the WTG. To do so, call the operator or Service. If clarification is not possible, initiate a service call. | 1 |  | Test on HIL |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 252
14025 | 12503 | Stop speed setpoint angle check | Rotor | WROT | Error | No |  |  | Operation Control | See only | See only | See only | See only | Covert | See only | See only | The hub controller has detected a high rotor speed. The WTG control system has specified an implausible setpoint pitch angle in conjunction with the rotor speed, which will not lead to a speed reduction in the case of an overspeed. Pitch back is triggered. | In case of repeated occurrence: inform TCC Level 2. Check rotor speed in the snapshot. If the status was caused by grid problems or gusty wind: Restart the WTG. Otherwise initiate a service call. | 2 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 253
14030 | 12504 | Speed actual angle check | Rotor | WROT | Warning | No |  |  | Operation Control | See only | See only | See only | See only | Covert | See only | See only | The hub controller has detected rotor overspeed. The hub controller checks whether the pitch system implements actual angles that lead to the speed being reduced. | No reaction required. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 254
14035 | 12505 | Stop speed actual angle check | Rotor | WROT | Error | No |  |  | Operation Control | See only | See only | See only | See only | Covert | See only | See only | The hub controller has detected rotor overspeed. The pitch system has not implemented the corresponding actual angles so that the speed is reduced. Pitch back is triggered. | In case of repeated occurrence: inform TCC Level 2. Check rotor speed in the snapshot. If the status was caused by grid problems or gusty wind: Restart the WTG. Otherwise initiate a service call. | 2 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 255
14040 | 12506 | Stop overspeed setpoint angle monitor | Rotor | WROT | Error | No |  |  | Operation Control | See only | See only | See only | See only | Covert | See only | See only | The hub controller has detected a high rotor speed and activated the "Overspeed setpoint angle monitor". Monitoring has shown that the WTG control system has specified an implausible setpoint pitch angle in conjunction with the rotor speed, which will not lead to a speed reduction in the case of an overspeed. Pitch back is triggered. | In case of repeated occurrence: inform TCC Level 2. Check rotor speed in the snapshot. If the status was caused by grid problems or gusty wind: Restart the WTG. Otherwise initiate a service call. | 2 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 256
14060 | 12507 | Gearbox speed WTG <> rotor speed | Rotor | WROT | Error | Yes |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The gearbox speed and the gear ratio are determined by the WTG control system. The rotor speed recorded by the hub controller multiplied with the gear ratio deviates from the gearbox speed of the WTG by more than 40rpm. Monitoring takes place starting at a rotor speed greater than or equal to 3 rpm. | In case of repeated occurrences: Initiate a service call. | 2 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 257
14070 | 12508 | Error rotor speed detection | Rotor | WROT | Error | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The two speeds, calculated using the signal "Rotor speed pulse" (digital input IX4.1, main box, module 4, DI232, terminal 1) with different debouncing times "Rotor speed" and "Rotor speed signal control" deviate from one another too much. Possible causes: - Distance of the inductive sensor is not set correctly. - Inductive sensor is defective. - The transmission section between the inductive sensor and the hub controller is defective. - EMC problems on the transmission section between the inductive sensor and the hub controller. | In case of repeated occurrences: Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 258
14301 | 12509 | Incorr. rotor speed calc. param. | Rotor | WROT | Error | No |  |  | Department | See only | See only | Service and Maintenance | See only | Covert | See only | See only | The function for calculating the rotor speed is incorrectly parameterized. | Initiate a service call. Load the correct parameter file. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 259
14310 | 12510 | 4-20mA position encoder rotor position | Rotor | WROT | Error | Yes |  |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Service Partner | See only | The current loop of the digital input "Rotor position encoder" (analog input ID6.8, main box, module 6, GIO212, terminals 52+53) is defective. | Initiate a service call. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 260
14320 | 12511 | Rotor position implaus. | Rotor | WROT | Error | Yes | *100ms |  | SCADA User | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The rotor position calculated by the hub controller is behaving implausibly. It is either, despite a rotor speed greater than 3 rpm, frozen at a fixed value, or it changes too slowly or too quickly. The rotor position is checked for expected change within a rotor speed range of 2 rpm to 16 rpm. Possible causes: Depending on the rotor position source - defect in the position encoder in the main box or in communication with the main box - defect of the acceleration sensor or the communication to it in at least one of the pitch converters - error in the communication to the pitch converters - software error in the pitch converter system | In the snapshot, check the progression of "Rotor pos. detection HC" in connection with the "Rotor speed". Inform the development departments of SCADA and Pitch Electrical Engineering. Initiate a service call if necessary | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 261
11160 | 12512 | Error blade coll. setp.angle rate at high speed setpoint | Rotor | WROT | Error | Yes |  |  | Department | See only | PMS Dispatcher | Service and Maintenance | See only | Covert | Covert | See only | The hub controller's setpoint rate monitoring at high speed setpoints has detected incorrect behavior. This can be caused by: - software error in the WTG controller - software error in the HC - communication failure between the HC and WTG control system | Shut down the WTG and inform SCADA development department. | 3 |  | Test on proto | turbine_operator_package: 'See Only' written as 'See only' | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 262
10110 | 12513 | SP additional braking speed limit | Rotor | WROT | Warning | No |  |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The maximum rotor speed permitted during pitch back or battery drive has been exceeded. For this reason, impulse braking of the rotor is requested briefly by the SLC of the HC. Possible causes for this include incorrect behavior of the WTG control system. This status code occurs as a result of braking procedures that take place beforehand. The preceding procedure must be inspected for the cause of the malfunction. | If this error occurs more frequently: Shut down the WTG and inform SCADA Control Engineering Development. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 263
10115 | 12514 | SP additional braking trigger | Rotor | WROT | Error | Yes | *0 ms |  | Operation Control | See only | See only | See only | Covert | Covert | Covert | See only | The maximum rotor speed permitted during pitch back or battery drive has been exceeded. For this reason, impulse braking of the rotor is requested by the SLC of the HC. StCd 10110 occurs as a result of braking procedures that take place beforehand. The preceding procedure must be inspected for the cause of the malfunction. Possible causes for this include incorrect behavior of the WTG control system. StCd 10115 also represents the permanent request of the rotor brake via the SLC. | If this error occurs more frequently: Shut down the WTG and inform SCADA Control Engineering Development. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 264
8410 | 13001 | IP duplicate in WF network | Wind farm | WPPD | Warning | No |  |  | Department | See only | Telenotdienst | Service and Maintenance | Preventive Maintenance | Covert | Ext. Service Provider | See only | The control system monitors for both Ethernet interfaces whether the own IP address is present more than once in the wind farm grid. If this is the case, the status code is activated. | Check the IP addresses in the wind farm on the basis of the IP diagram. | 3 |  | Test on proto |  | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 265
14321 | 12515 | UCAP capacity low axis 1 | Rotor | WROT | [17 empty] | type missing in the source; new number taken from the earlier numbering proposal (hc-numbering-proposal.xlsx) on the owner's instruction 2026-10-27; approval of the three roles pending | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 266
14322 | 12516 | UCAP capacity low axis 2 | Rotor | WROT | [15 empty] | HIL: 10 days |  | type missing in the source; new number taken from the earlier numbering proposal (hc-numbering-proposal.xlsx) on the owner's instruction 2026-10-27; approval of the three roles pending | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 267
14323 | 12517 | UCAP capacity low axis 3 | Rotor | WROT | [15 empty] | Proto: 15 days |  | type missing in the source; new number taken from the earlier numbering proposal (hc-numbering-proposal.xlsx) on the owner's instruction 2026-10-27; approval of the three roles pending | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 268
14324 | 12518 | Pitch system hardware mismatch | Rotor | WROT | [17 empty] | type missing in the source; new number taken from the earlier numbering proposal (hc-numbering-proposal.xlsx) on the owner's instruction 2026-10-27; approval of the three roles pending | PROPOSED | HC Status Code Number.xlsx, sheet SW_8_30_2, row 269

## HC_groups
functional_group | logical_node | gid | new_range | records_in_source
Blade | WROT | 12 | 001-050 | 25
Batteries | WROT | 12 | 051-200 | 51
Control System | WTUR | 11 | 001-100 | 36
Field Bus | WTUR | 11 | 101-150 | 8
Pitch | WROT | 12 | 201-250 | 35
Pitch Control | WROT | 12 | 251-300 | 9
Pitch Drivers | WROT | 12 | 301-400 | 33
Pitch Converter | WROT | 12 | 401-500 | 45
Rotor | WROT | 12 | 501-600 | 14
System | WTUR | 11 | 151-200 | 7
Wind Farm | WROT | 13 | 001-100 | 1

## Glossary
german | english | note
umrichter | converter, conv.
umr. | conv., converter
sicherung | fuse
ausgelöst | tripped, trip
kommunikation | comm, communication
fehler | error, fault, failure
störung | fault, failure, error
rotor | rotor
überdrehzahl | overspeed
drehzahl | speed, rpm
test | test
stopp | stop
sollwinkel | setpoint angle, angle setpoint, angle sp
winkel | angle
nicht bereit | not ready
temperatur | temp, temperature
druck | press, pressure
öl | oil
getriebe | gearbox, gear, gearb
generator | generator, gen
netz | grid, mains
spannung | voltage, volt
strom | current
azimut | yaw
blatt | blade
turm | tower
gondel | nacelle
bremse | brake
heizung | heating, heater
lüfter | fan
pumpe | pump
schalter | switch, breaker, cb
überwachung | monitoring, monit.
grenzwert | limit
sollwert | setpoint, setp.
istwert | actual value, actual
batterie | batter
hydraulik | hydraulic, hyd.
windgeschwindigkeit | wind speed, windspeed
kühl | cool
schmier | lubric, lube
leistung | power
frequenz | frequency, freq
not-aus | emergency stop, e-stop, emergency
watchdog | watchdog
neustart | reboot, restart
reboot | reboot

## Approvals
date | family | legacy_number | new_number | requested_by | stcd_owner | chief_engineer | administrator | decision
One row per new number. All three approvals (name and date) are needed before the status of the number is set to APPROVED.

## Lists
status | type | family
PROPOSED | Error | MC
FROM_PROGRAM | Warning | HC
APPROVED | Info
ISSUED
REJECTED